ISTEC TRAINING · ROOT CAUSE ANALYSIS · CAUSE-AND-EFFECT FAULT TREE

# Diesel overfill of tank T-101 during night transfer

RCA-EX-01 · Coastal Fuel Terminal (fictional) · Worked example

| Item | Detail |
| --- | --- |
| Date and time | 2026-09-18, 03:40 |
| Location | Tank T-101, bund B-1 |
| Investigator | Lead investigator |
| Team | Lead investigator; Operations superintendent; Instrument technician; HSE adviser |
| Status | In review |

# 1. Description of the incident

During a night ship-to-tank transfer, diesel overflowed from tank T-101 into bund B-1. About 14 m³ was contained in the bund and recovered; no injuries and no off-site release.

# 2. Conclusion

The transfer was not stopped because the level gauge LT-101 froze at 78 % and the single night-shift operator, busy with a ship arrival, did not cross-check the level. The independent high-high trip LSHH-101 failed because its float was seized; proof testing had dropped out of the maintenance system. The independent alarm LAH-102 was probably missed in an alarm flood (still being confirmed).

## Root causes

E-06 LSHH-101 level switch failed on demand (float stuck) (Maintenance)  [Confirmed]

Why: Proof testing of tank overfill switches dropped from the CMMS schedule; no tracking of overdue SIS tests.

## Causal factors

E-04 LT-101 servo gauge displacer stuck (frozen reading) (Equipment / hardware)  [Confirmed]

Why: Gauge not in the planned maintenance system after the 2024 replacement.

E-03 Level cross-check not done during the transfer (Human performance)  [Confirmed]

Why: Transfer procedure has no hold point for cross-checking level near the end of a transfer.

E-08 Control-room operator did not respond to the independent high-level alarm LAH-102 (Human performance)  [Likely]

Why: Alarm flood during ship arrival; LAH-102 has the same priority as nuisance alarms.

## Contributing factors

H-01 Single operator on night shift, also handling a ship arrival (Organisation / management)  [Confirmed]

Why: Night manning reduced from two to one in 2025 without a management-of-change review.

# 3. Fault tree

Values given the evidence (ruled out = 0, confirmed = 1). “Given incident” = probability that an unresolved cause contributed, given the top event happened.

# 4. Hypotheses and evidence

| Code | Cause / event | Type | Status | Evidence | Test (open items) |
| --- | --- | --- | --- | --- | --- |
| TOP | Diesel overflowed from tank T-101 into the bund during a night transfer | AND gate | Confirmed | About 14 m³ diesel in bund B-1 at 03:40 (shift log, CCTV, photos P1–P9). Bund held; no off-site release. |  |
| E-01 | Ship-to-tank transfer into T-101 under way (demand on the overfill controls) | Basic event | Confirmed | Transfer TR-2611 from MV Coral started 22:10. |  |
| G-02 | Transfer not stopped before the tank was full | OR gate | Confirmed | Pumping continued until 03:38, when the ship stopped on radio call. |  |
| G-04 | Operator unaware the tank was nearly full | AND gate | Confirmed | Operator interview: believed level was 78 % at 03:20. |  |
| G-08 | Level gauge LT-101 indicated lower than the actual level | OR gate | Confirmed | DCS trend flat at 78 % from 01:55 while dip showed 100 %. |  |
| E-04 | LT-101 servo gauge displacer stuck (frozen reading) | Basic event | Confirmed | Gauge found stuck at 78 % on inspection; displacer wire fouled with wax (photo P12). |  |
| E-09 | LT-101 calibration drift | Undeveloped event | Ruled out | Calibration certificate 6 weeks old; as-found check within 2 mm. |  |
| G-07 | Operator did not cross-check the level by an independent means | INHIBIT gate | Confirmed | No radar or dip cross-check recorded in the 4-hourly round. |  |
| E-03 | Level cross-check not done during the transfer | Basic event | Confirmed | Round sheet blank for 02:00; operator was at jetty 2 for MV Delta arrival. |  |
| H-01 | Single operator on night shift, also handling a ship arrival | Condition / house event | Confirmed | Roster: one operator 18:00–06:00; MV Delta berthed 01:50. |  |
| E-05 | Transfer nomination larger than available ullage (planning error) | Basic event | Ruled out | Nomination 2 400 m³ against 2 610 m³ ullage: calculation checked and correct. |  |
| G-03 | Independent overfill protection did not stop the transfer | AND gate | Confirmed | No trip of XV-101 recorded; LAH-102 alarm acknowledged at 03:12. |  |
| G-05 | High-high level trip LSHH-101 / XV-101 failed | OR gate | Confirmed | XV-101 stayed open; LSHH-101 did not change state when flooded. |  |
| E-06 | LSHH-101 level switch failed on demand (float stuck) | Basic event | Confirmed | Float found seized by corrosion product (photo P15). Last proof test 30 months ago (CMMS). |  |
| E-07 | Trip left bypassed after maintenance | Basic event | Ruled out | Bypass log and DCS event list: no bypass active on LSHH-101. |  |
| G-09 | High-level alarm LAH-102 did not lead to the transfer being stopped | OR gate | Confirmed | Alarm at 03:12; pumping stopped 03:38 (26 min later). |  |
| E-08 | Control-room operator did not respond to the independent high-level alarm LAH-102 | Basic event | Likely | LAH-102 acknowledged at 03:12; 41 other alarms in the same 20 minutes (preliminary journal). | Retrieve alarm journal 02:30–03:40 and interview control-room operator about alarm load. (Lead investigator, 2026-10-20) |
| E-10 | Stop instruction to the ship by radio not received or delayed | Basic event | Unverified |  | Obtain the jetty and ship VHF recordings for 03:10–03:40; interview the ship duty officer. (HSE adviser, 2026-10-22) |

## Open hypotheses ranked by likelihood given the incident

| Cause | Status | P(contributed ¦ incident) | Planned test |
| --- | --- | --- | --- |
| E-08 Control-room operator did not respond to the independent high-level alarm LAH-102 | Likely | 97 % | Retrieve alarm journal 02:30–03:40 and interview control-room operator about alarm load. |
| E-10 Stop instruction to the ship by radio not received or delayed | Unverified | 3 % | Obtain the jetty and ship VHF recordings for 03:10–03:40; interview the ship duty officer. |

# 5. Quantification

Top event before the evidence: 1.5E-03 /yr. Given the evidence: 5.3 /yr.

| Code | Event | Source | Library default | Value used | Note |
| --- | --- | --- | --- | --- | --- |
| E-01 | Ship-to-tank transfer into T-101 under way (demand on the overfill controls) | Manual value |  | 52 /yr | About one transfer a week into T-101 (2025 transfer records). |
| E-04 | LT-101 servo gauge displacer stuck (frozen reading) | Equipment failure on demand | Transmitter fails, reading frozen or wrong (annual test) – 0.01 (GENERIC) | 0.01 |  |
| E-09 | LT-101 calibration drift | Manual value |  | 1.0E-03 | Screening estimate. |
| E-03 | Level cross-check not done during the transfer | Human error probability | HEART D: fairly simple task performed rapidly or given scant attention – 0.09 (HEART) | 0.2 (edited) | HEART D nominal 0.09 raised for night shift, single operator handling a ship arrival (EPCs: time shortage, high workload). |
| E-05 | Transfer nomination larger than available ullage (planning error) | Human error probability | Omit a step from a written procedure, no check-off – 3.0E-03 (THERP) | 3.0E-03 |  |
| E-06 | LSHH-101 level switch failed on demand (float stuck) | Equipment failure on demand | Level / pressure switch fails on demand (annual test) – 0.01 (GENERIC) | 0.05 (edited) | Library 0.01 assumes an annual proof test; LSHH-101 test was 18 months overdue, so PFD scaled up about ×5. |
| E-07 | Trip left bypassed after maintenance | Human error probability | Fail to restore equipment (bypass, valve, guard) after maintenance – 3.0E-03 (HEART F / THERP) | 3.0E-03 |  |
| E-08 | Control-room operator did not respond to the independent high-level alarm LAH-102 | Safeguard / IPL PFD | Operator response to alarm, ≥10 min available, trained, procedure – 0.1 (CCPS-LOPA) | 0.1 |  |
| E-10 | Stop instruction to the ship by radio not received or delayed | Human error probability | Error in recalling or passing on a verbal instruction (several items) – 3.0E-03 (THERP) | 3.0E-03 |  |

## Credible causal combinations (minimal cut sets)

| # | Causes | Status | Before evidence | Given evidence | Share |
| --- | --- | --- | --- | --- | --- |
| 1 | E-01 Ship-to-tank transfer into T-101 under way (demand on the overfill controls) E-03 Level cross-check not done during the transfer E-04 LT-101 servo gauge displacer stuck (frozen reading) E-06 LSHH-101 level switch failed on demand (float stuck) E-08 Control-room operator did not respond to the independent high-level alarm LAH-102 H-01 Single operator on night shift, also handling a ship arrival | likely | 5.2E-04 /yr | 5.2 /yr | 97 % |
| 2 | E-01 Ship-to-tank transfer into T-101 under way (demand on the overfill controls) E-10 Stop instruction to the ship by radio not received or delayed E-03 Level cross-check not done during the transfer E-04 LT-101 servo gauge displacer stuck (frozen reading) E-06 LSHH-101 level switch failed on demand (float stuck) H-01 Single operator on night shift, also handling a ship arrival | open | 1.6E-05 /yr | 0.16 /yr | 3 % |

# 6. Corrective actions

| # | Addresses | Action | Control | Owner | Due | Status |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | E-06 LSHH-101 level switch failed on demand (float stuck) | Restore proof testing of all tank overfill switches (LSHH) in the CMMS and test LSHH-101/201/301 within 14 days. | Engineering | Maintenance Manager | 2026-10-31 | Open |
| 2 | E-06 LSHH-101 level switch failed on demand (float stuck) | Add an overdue-SIS-test KPI to the monthly management review. | Administrative | Terminal Manager | 2026-12-15 | Open |
| 3 | E-04 LT-101 servo gauge displacer stuck (frozen reading) | Add servo gauge LT-101 (and sister gauges) to the planned maintenance system with a 6-monthly displacer inspection. | Engineering | Instrument Supervisor | 2026-11-15 | Open |
| 4 | E-03 Level cross-check not done during the transfer | Add a level cross-check hold point (radar vs servo, at 85 % and 95 %) to the transfer procedure. | Administrative | Operations Superintendent | 2026-11-01 | Open |
| 5 | H-01 Single operator on night shift, also handling a ship arrival | Carry out a management-of-change review of single-operator night manning during ship arrivals. | Administrative | Terminal Manager | 2026-11-30 | Open |
| 6 | E-08 Control-room operator did not respond to the independent high-level alarm LAH-102 | Re-prioritise LAH-102 and other independent overfill alarms as high priority; rationalise nuisance alarms. | Engineering | Control Systems Engineer | 2027-01-31 | Open |

# 7. Lessons learned

• Independent overfill protection is only independent if it is tested.

• Manning changes need a management-of-change review that covers peak workload, such as a ship arrival during a transfer.

# 8. Tree consistency check

• WARNING: G-09 “High-level alarm LAH-102 did not lead to the transfer being stopped” is confirmed but none of its causes is confirmed yet. Find which one occurred.

# Review and sign-off

| Lead investigator | Reviewer | Accountable manager |
| --- | --- | --- |
| Name, signature, date | Name, signature, date | Name, signature, date |

Screening values from generic sources: CCPS, Layer of Protection Analysis (2001); Guidelines for Initiating Events and IPLs in LOPA (2015); IEC 61511-1, safety instrumented systems for the process industry sector (SIL bands); Swain & Guttmann, NUREG/CR-1278 Handbook of Human Reliability Analysis (1983); Williams, HEART – Human Error Assessment and Reduction Technique (generic task types); Typical generic process-industry per-demand failure values (CCPS CPQRA and reliability handbooks). They rank hypotheses; they are not design data.