## Cover
FMECA WORKBOOK
Failure Modes, Effects and Criticality Analysis – companion to the HAZOP Study Workbook (IEC 60812 approach)
Legend: | Yellow = enter / select data | Grey = formula (do not overwrite) | Blue = returned from another sheet
STUDY DETAILS
Study title | FMECA – Natural gas distribution network (worked example)
Company / site | Hadeed – integrated DRI-EAF steel works (illustrative example)
Plant / unit / area | Utilities – natural gas receiving, pressure reduction and plant distribution
Related HAZOP study (document no.) | HZ-EX-GN-001
Study type | FMECA – existing plant
Document number | FM-EX-GN-001
Revision | A
Study start date | 2026-10-15
Study end date | 2026-10-16
Scope – systems included | S01–S08 = HAZOP nodes N01–N08: GRMS, heaters + PRS-1, MP ring main, DS-2 (DRI), DS-3 (melt shop), reheat furnace fuel train + BMS, purge / vent, gas detection & ESD
Exclusions | As the HAZOP (supplier pipeline, reformer internals, O2 plant, N2 generation)
Level of analysis | Equipment / maintainable item
Operating context | Continuous utility service; duty / standby filter-separators, heaters and regulator runs; protection systems on demand (proof-tested). Failure data illustrative – see the fault trees FT-GN-01/02/03
Facilitator | A. Facilitator
Scribe | B. Scribe
Rating method | Severity, Occurrence, Detection 1–10; RPN = S x O x D; AIAG-VDA Action Priority (see 'Rating Scales')
Number of systems
Number of equipment items
STUDY TEAM
Name | Company | Discipline / role | Sessions / days attended | Signature
A. Facilitator | Istec | Facilitator | Days 1–2
B. Scribe | Istec | Scribe | Days 1–2
E. Instrument | Maintenance | Electrical / instrument technician | Days 1–2
F. Mechanical | Maintenance | Maintenance engineer / planner | Days 1–2
J. Reliability | Maintenance | Reliability engineer | Days 1–2
D. Operator | Utilities | Operations representative | Days 1–2
APPROVAL
| Name | Position | Signature | Date
Prepared by
Reviewed by
Approved by
WORKBOOK CONTENTS
Cover | Study details, team, approval
Reference Docs | Drawings, equipment data, maintenance history and reliability data used in the study
Systems | System list: function, operating context, boundaries, drawings, related HAZOP nodes
Equipment Register | Equipment tags per system with equipment type (drives the drop-downs on the system sheets)
Lists | Drop-down sources: equipment types, components, failure modes, causes / mechanisms, detection methods (editable)
Rating Scales | Severity, Occurrence, Detection 1–10 scales, RPN / severity thresholds and Action Priority table (editable)
Summary | Failure modes, Action Priority counts, highest RPN and open actions per system
System 01 … System 10 | One FMECA worksheet per system – one row per failure mode

## Reference Docs
REFERENCE DOCUMENT REGISTER
Pre-filled with a typical FMECA checklist – delete or add rows as required.
Ref | Category | Document number | Title / description | Revision | Date | Owner / custodian | Status | Applicable systems | Comments
REF-01 | Drawings | P&ID-GN-1001 | Gas receiving & metering station (GRMS) P&ID | A |  | Utilities | Available | S01
REF-02 | Drawings | P&ID-GN-1101 | Gas heaters and pressure reduction station PRS-1 P&ID | A |  | Utilities | Available | S02
REF-03 | Drawings | P&ID-GN-1201/1202 | MP ring main and pipe-rack routing | A |  | Utilities | Available | S03
REF-04 | Drawings | P&ID-GN-2001 | DRI plant district station DS-2 | A |  | Utilities | Available | S04
REF-05 | Drawings | P&ID-GN-3001 | Melt shop district station DS-3, oxy-fuel burners and ladle preheaters | A |  | Utilities | Available | S05
REF-06 | Drawings | P&ID-GN-4001 | Rolling-mill reheat furnace fuel gas train and BMS | A |  | Utilities | Available | S06
REF-07 | Drawings | P&ID-GN-1301 | Vent stack, blowdown and N2 purge connections | A |  | Utilities | Available | S07
REF-08 | Drawings | C&E-GN-1000 | ESD / F&G cause-and-effect charts | A |  | Utilities | Available | S01, S02, S08
REF-09 | Drawings | HAC-GN-001 | Hazardous area classification – gas network | A |  | Utilities | Available | S01, S02, S03, S07
REF-10 | Other | DB-GN-001 | Gas network design basis (pressures, set points, MDMT) | A |  | Utilities | Available | S01, S02, S03
REF-11 | Other | RS-GN-001 | Relief and overpressure protection study | A |  | Utilities | Available | S01, S02, S07
REF-12 | Other | SRS-GN-001 | Safety requirements specification – gas ESD and furnace BMS | A |  | Utilities | Available | S06, S08
REF-13 | Other | SDS-NG-001 | Natural gas safety data sheet; gas supply quality specification | A |  | Utilities | Available | S01
REF-14 | Other | OP-GN-010 | Pigging procedure (pig receiver PR-1001) | A |  | Utilities | Available | S01, S07
REF-15 | Other | OP-GN-020 | Purging and gas-in / gas-out procedure | A |  | Utilities | Available | S03, S07
REF-16 | Other | OP-RM-040 | Reheat furnace light-off and shutdown procedure | A |  | Utilities | Available | S06
REF-17 | Other | HZ-GN-2019 | Previous gas network HAZOP (2019) and close-out status | A |  | Utilities | Available | S01, S02, S03
REF-18 | Other | INC-GN-LOG | Gas incident / near-miss log (last 5 years) | A |  | Utilities | Available | S03, S05, S06
REF-19 | Other | HZ-EX-GN-001 | HAZOP study (this example) – HAZOP Study Manager file and workbook | A |  | Utilities | Available | S01–S08
REF-20 | Other | FT-GN-01/02/03 | Fault trees – PRS overpressure, gas detection & ESD, reheat furnace BMS | A |  | Utilities | Available | S02, S08, S06
REF-21 | Other | OREDA / CCPS | Generic reliability data used for the illustrative failure rates | A |  | Utilities | Available
REF-22
REF-23
REF-24
REF-25
REF-26
REF-27
REF-28
REF-29
REF-30
REF-31
REF-32
REF-33
REF-34
REF-35
REF-36
REF-37
REF-38
REF-39
REF-40

## Systems
SYSTEM LIST
One row per system. System title (column C) feeds the drop-down at the top of each FMECA worksheet and the Equipment Register.
System No. | System name | System title (auto) | Function / performance standard | Operating context (duty, redundancy, environment) | System boundaries | P&IDs / drawings | Related HAZOP node(s) | Comments
S01 | Gas receiving & metering station (GRMS) |  | Receive, filter and meter up to 120 000 Sm3/h at 35–42 barg; isolate on ESD within 30 s | Continuous; 2 x 100 % filter-separators and meter runs; outdoor, hot / dusty | IJ-1001 to heater inlet | P&ID-GN-1001 | HAZOP N01
S02 | Gas heaters H-1101A/B and pressure reduction station PRS-1 |  | Heat gas to keep outlet ≥ 5 °C; hold 7.0 barg; never exceed 10 barg downstream | Continuous; 2 x 100 % heaters and regulator runs (A duty, B standby); monitor + slam-shut protection proof-tested | Heater inlet to ESDV-1107 | P&ID-GN-1101 | HAZOP N02
S03 | MP ring main (7 barg) and pipe racks |  | Distribute 7 barg gas without loss of containment | Continuous; buried crossings with impressed-current CP; racks crossing roads and crane areas | ESDV-1107 to district-station inlets | P&ID-GN-1201/1202 | HAZOP N03
S04 | DRI plant gas supply – district station DS-2 |  | Supply reformer fuel and process-gas make-up at 4.5 barg; prevent reverse flow of process gas | Continuous; 2 x 100 % regulators | ESDV-2001 to FCV-2004 / XV-2008 | P&ID-GN-2001 | HAZOP N04
S05 | Melt shop gas supply – DS-3, EAF oxy-fuel burners and ladle preheaters |  | Supply NG at 2 barg; prevent O2 back-flow; shut off on flame failure | Intermittent; hot, dusty, molten-metal splash zone | ESDV-3001 to burners | P&ID-GN-3001 | HAZOP N05
S06 | Rolling-mill reheat furnace fuel gas train and burner management |  | Fire only when safe; shut off fuel within 1 s on flame failure (target SIL 2 – see R-010) | Continuous firing with cold light-offs after outages; BMS proof-tested annually | PCV-4001 to burners B-4020 | P&ID-GN-4001 | HAZOP N06
S07 | Purge, vent, blowdown and maintenance isolation |  | Depressurise, purge and isolate safely | Used during maintenance, pigging and gas-in / gas-out | VS-1301, BDV-1302, SB-1303, N2-1304 | P&ID-GN-1301 | HAZOP N07
S08 | Gas detection, F&G and ESD system |  | Detect a release and close ESDV-1001 / ESDV-1107 (PFDavg per FT-GN-02) | Standby protection; 2oo3 detectors; UPS 30 min; proof-tested | Detectors, HS-1000, UCP-1000, UPS-1000 | C&E-GN-1000 | HAZOP N08
S09
S10
S11
S12
S13
S14
S15
S16
S17
S18
S19
S20
S21
S22
S23
S24
S25
S26
S27
S28
S29
S30

## Equipment Register
EQUIPMENT REGISTER
List every equipment item in scope against its system. Equipment type selects the component and failure-mode lists on the FMECA sheets.
Item | System | Equipment tag | Equipment description | Equipment type | Manufacturer / model | Configuration | Function | Comments
1 | S01 – Gas receiving & metering station (GRMS) | IJ-1001 | Inlet insulating joint and buried inlet piping | Piping, flanges & hoses |  | Single | Electrically isolate the plant from the supplier pipeline CP
2 | S01 – Gas receiving & metering station (GRMS) | ESDV-1001 | GRMS inlet ESD valve | Isolation / ESD valve |  | Single | Isolate the supplier pipeline on ESD (fail closed)
3 | S01 – Gas receiving & metering station (GRMS) | PR-1001 | Pig receiver with quick-opening closure | Pressure vessel / separator / column |  | Single | Receive pigs from the supplier pipeline
4 | S01 – Gas receiving & metering station (GRMS) | F-1002A | Filter-separator A | Pressure vessel / separator / column |  | Duty | Remove liquids and solids
5 | S01 – Gas receiving & metering station (GRMS) | F-1002B | Filter-separator B | Pressure vessel / separator / column |  | Standby | Remove liquids and solids
6 | S01 – Gas receiving & metering station (GRMS) | FT-1003A | Ultrasonic custody meter A | Instrument – transmitter / switch |  | Duty | Custody-transfer metering
7 | S01 – Gas receiving & metering station (GRMS) | AT-1004 | Gas chromatograph | Analyser / gas detector |  | Single | Composition, Wobbe and H2S
8 | S01 – Gas receiving & metering station (GRMS) | PSV-1006A | Filter-separator A relief valve | Pressure relief device (PSV / rupture disc) |  | Single | Fire-case / thermal relief
9 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | H-1101A | Water-bath gas heater A | Burner / combustion system |  | Duty | Pre-heat gas against Joule–Thomson cooling
10 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | H-1101B | Water-bath gas heater B | Burner / combustion system |  | Standby | Pre-heat gas against Joule–Thomson cooling
11 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | TT-1101 | Heater gas outlet temperature transmitter | Instrument – transmitter / switch |  | Single | TIC-1101 control and TSL-1101 alarm
12 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | SSV-1102A | Slam-shut valve run A (OPSO 8.5 barg) | Isolation / ESD valve |  | Duty | Close run A on overpressure
13 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | PCV-1103A | Monitor regulator run A (7.5 barg) | Control valve |  | Duty | Take over pressure control if the active regulator fails open
14 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | PCV-1104A | Active regulator run A (7.0 barg) | Control valve |  | Duty | Control PRS outlet pressure
15 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | PSV-1105 | PRS token relief valve (9.0 barg) | Pressure relief device (PSV / rupture disc) |  | Single | Relieve lock-up creep
16 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | PT-1106 | PRS outlet pressure transmitter | Instrument – transmitter / switch |  | Single | PAH-1106 / PAL alarms
17 | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | ESDV-1107 | PRS outlet ESD valve | Isolation / ESD valve |  | Single | Isolate the MP header inventory from the PRS on ESD
18 | S03 – MP ring main (7 barg) and pipe racks | L-1200 | MP ring main 24" (racks and buried crossings) | Piping, flanges & hoses |  | Single | Contain and distribute 7 barg gas
19 | S03 – MP ring main (7 barg) and pipe racks | XV-1201 | Sectionalising valve 1 (remote operated) | Isolation / ESD valve |  | Single | Sectional isolation of the ring main
20 | S03 – MP ring main (7 barg) and pipe racks | PT-1210 | MP header pressure transmitter | Instrument – transmitter / switch |  | Single | PAL-1210 leak / supply-loss alarm
21 | S03 – MP ring main (7 barg) and pipe racks | CP-1200 | CP transformer-rectifier | Transformer |  | Single | Impressed-current cathodic protection
22 | S04 – DRI plant gas supply – district station DS-2 | ESDV-2001 | DS-2 inlet ESD valve | Isolation / ESD valve |  | Single | Isolate DRI plant supply
23 | S04 – DRI plant gas supply – district station DS-2 | FCV-2004 | Reformer fuel gas flow control valve | Control valve |  | Single | Control reformer firing
24 | S04 – DRI plant gas supply – district station DS-2 | XV-2008 | Process-gas NG make-up shut-off valve (with double NRV) | Isolation / ESD valve |  | Single | Prevent reverse flow of process gas into NG
25 | S04 – DRI plant gas supply – district station DS-2 | PSLL-2006 | Reformer fuel low-low pressure switch | Instrument – transmitter / switch |  | Single | Trip reformer burners on low gas pressure
26 | S05 – Melt shop gas supply – DS-3, EAF oxy-fuel burners and ladle preheaters | SSV-3003 | DS-3 slam-shut valve | Isolation / ESD valve |  | Single | Overpressure shut-off of DS-3
27 | S05 – Melt shop gas supply – DS-3, EAF oxy-fuel burners and ladle preheaters | NRV-3010 | NG non-return valve + flashback arrestor (oxy-fuel burner) | Isolation / ESD valve |  | Single | Prevent O2 back-flow into the NG line
28 | S05 – Melt shop gas supply – DS-3, EAF oxy-fuel burners and ladle preheaters | XV-3011 | Oxy-fuel burner NG shut-off valve | Isolation / ESD valve |  | Single | Shut off NG on burner trip
29 | S05 – Melt shop gas supply – DS-3, EAF oxy-fuel burners and ladle preheaters | LPH-3020 | Ladle preheater burner system | Burner / combustion system |  | Single | Preheat ladles safely
30 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | XV-4002A | Reheat furnace safety shut-off valve A | Isolation / ESD valve |  | Duty | Shut off fuel on trip (1oo2 with XV-4002B)
31 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | XV-4002B | Reheat furnace safety shut-off valve B | Isolation / ESD valve |  | Duty | Shut off fuel on trip (1oo2 with XV-4002A)
32 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | XV-4003 | Vent valve between the SSOVs (DBB) | Isolation / ESD valve |  | Single | Vent the space between the SSOVs
33 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | VPS-4004 | Valve proving system | Instrument – transmitter / switch |  | Single | Prove SSOV tightness before light-off
34 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | PSLL-4005 | Low-low fuel gas pressure switch | Instrument – transmitter / switch |  | Single | Trip on low gas pressure
35 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | PSHH-4006 | High-high fuel gas pressure switch | Instrument – transmitter / switch |  | Single | Trip on high gas pressure
36 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | FN-4007 | Combustion air fan | Fan / blower (incl. ID fan) |  | Single | Supply combustion air
37 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | FSLL-4008 | Low-low combustion air flow switch | Instrument – transmitter / switch |  | Single | Trip on low air flow
38 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | BS-4010 | UV flame scanners (one per burner) | Instrument – transmitter / switch |  | Single | Detect loss of flame
39 | S06 – Rolling-mill reheat furnace fuel gas train and burner management | BMS-4000 | Burner management system logic solver | Control system / SIS logic solver |  | Single | Purge, light-off and flame-failure logic
40 | S07 – Purge, vent, blowdown and maintenance isolation | VS-1301 | PRS vent stack | Piping, flanges & hoses |  | Single | Disperse vented gas safely
41 | S07 – Purge, vent, blowdown and maintenance isolation | BDV-1302 | PRS blowdown valve | Isolation / ESD valve |  | Single | Depressurise the PRS
42 | S07 – Purge, vent, blowdown and maintenance isolation | N2-1304 | N2 purge connection (removable spool / hose) | Piping, flanges & hoses |  | Single | Purge with N2 for gas-in / gas-out
43 | S08 – Gas detection, F&G and ESD system | GD-1110A | PRS shelter gas detector A (2oo3) | Analyser / gas detector |  | Duty | Detect gas release
44 | S08 – Gas detection, F&G and ESD system | GD-1110B | PRS shelter gas detector B (2oo3) | Analyser / gas detector |  | Duty | Detect gas release
45 | S08 – Gas detection, F&G and ESD system | GD-1110C | PRS shelter gas detector C (2oo3) | Analyser / gas detector |  | Duty | Detect gas release
46 | S08 – Gas detection, F&G and ESD system | UCP-1000 | SIS logic solver (gas ESD) | Control system / SIS logic solver |  | Single | Execute the ESD cause & effects
47 | S08 – Gas detection, F&G and ESD system | HS-1000 | Manual ESD push buttons | Instrument – transmitter / switch |  | Single | Manual ESD initiation
48 | S08 – Gas detection, F&G and ESD system | UPS-1000 | UPS for SIS / F&G | Variable speed drive / UPS |  | Single | 30 min back-up power
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200

## Lists
DROP-DOWN LISTS
Editable. To add a component or failure mode, INSERT a row inside its equipment-type block (blocks must stay together). Failure-mode codes follow ISO 14224 where applicable.
Equipment types | Equipment type | Component / maintainable item | Equipment type | Failure mode | Failure causes / mechanisms | Detection methods | Action / task type | Document category
Centrifugal pump | Centrifugal pump | Impeller | Centrifugal pump | FTS – Fail to start on demand | 1.0 Mechanical failure – general | Online vibration monitoring with alarm | Condition monitoring task | Drawings
Positive displacement pump | Centrifugal pump | Casing | Centrifugal pump | STP – Fail to stop on demand | 1.1 Leakage | Periodic vibration analysis (route) | Time-based maintenance / overhaul | Equipment data
Centrifugal compressor | Centrifugal pump | Shaft | Centrifugal pump | UST – Spurious stop | 1.2 Vibration | Infrared thermography | Failure-finding / proof test | Maintenance history
Reciprocating compressor | Centrifugal pump | Bearings | Centrifugal pump | BRD – Breakdown | 1.3 Clearance / alignment failure | Oil / lubricant analysis | Operator round / inspection | Reliability data
Fan / blower (incl. ID fan) | Centrifugal pump | Mechanical seal | Centrifugal pump | LOO – Low output (flow / head) | 1.4 Deformation | Ultrasonic thickness / NDT inspection | Redesign / modification (MOC) | Procedures
Electric motor | Centrifugal pump | Coupling | Centrifugal pump | HIO – High output | 1.5 Looseness | Acoustic emission / ultrasonic leak detection | Spares holding | Previous studies
Gearbox | Centrifugal pump | Wear rings | Centrifugal pump | ELP – External leakage – process medium | 1.6 Sticking / seizure | Motor current signature analysis | Procedure / training | Other
Belt conveyor | Centrifugal pump | Baseplate / holding-down | Centrifugal pump | ELU – External leakage – utility medium | 2.0 Material failure – general | Partial discharge / insulation testing | Run to failure (accepted)
Pressure vessel / separator / column | Centrifugal pump | Lubrication system | Centrifugal pump | INL – Internal leakage / recirculation | 2.1 Cavitation | Process alarm (DCS) | Further study
Shell & tube heat exchanger | Centrifugal pump | Suction strainer | Centrifugal pump | VIB – Vibration | 2.2 Corrosion (general / pitting / CUI) | Protective trip / interlock
Atmospheric storage tank | Positive displacement pump | Rotors / gears / pistons | Centrifugal pump | NOI – Noise | 2.3 Erosion | Performance monitoring (flow, ΔP, efficiency)
Piping, flanges & hoses | Positive displacement pump | Suction / discharge valves | Centrifugal pump | OHE – Overheating | 2.4 Wear | Operator rounds – visual / sensory
Control valve | Positive displacement pump | Packing / seals | Centrifugal pump | PDE – Parameter deviation | 2.5 Breakage / fracture | Proof test / function test
Isolation / ESD valve | Positive displacement pump | Bearings | Centrifugal pump | STD – Structural deficiency | 2.6 Fatigue (mechanical / thermal) | Leak detection system (flow in / out)
Pressure relief device (PSV / rupture disc) | Positive displacement pump | Drive (gearbox / coupling) | Centrifugal pump | PLU – Plugged / choked | 2.7 Overheating | Gas / fire detection
Instrument – transmitter / switch | Positive displacement pump | Pulsation damper | Centrifugal pump | OTH – Other | 2.8 Burst | Shell temperature scanning (refractory)
Analyser / gas detector | Positive displacement pump | Integral relief valve | Positive displacement pump | FTS – Fail to start on demand | 3.0 Instrument failure – general | Rope / brake / structural inspection (cranes)
Control system / SIS logic solver | Positive displacement pump | Casing | Positive displacement pump | STP – Fail to stop on demand | 3.1 Control failure | Calibration check
Transformer | Centrifugal compressor | Impellers | Positive displacement pump | UST – Spurious stop | 3.2 No signal / indication / alarm | Shutdown inspection
Switchgear / MCC / circuit breaker | Centrifugal compressor | Rotor / shaft | Positive displacement pump | BRD – Breakdown | 3.3 Faulty signal / indication / alarm | None – failure evident only on occurrence
Variable speed drive / UPS | Centrifugal compressor | Journal and thrust bearings | Positive displacement pump | LOO – Low output (flow / head) | 3.4 Out of adjustment / calibration drift | None – hidden failure
Hydraulic power unit / system | Centrifugal compressor | Dry gas / oil seals | Positive displacement pump | HIO – High output | 3.5 Software / configuration failure
Overhead crane / hoist (incl. ladle crane) | Centrifugal compressor | Lube oil system | Positive displacement pump | ELP – External leakage – process medium | 3.6 Common cause / mode failure
Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Centrifugal compressor | Anti-surge valve and control | Positive displacement pump | ELU – External leakage – utility medium | 4.0 Electrical failure – general
Refractory lining (furnace, ladle, tundish, kiln) | Centrifugal compressor | Casing | Positive displacement pump | INL – Internal leakage / recirculation | 4.1 Short circuiting
Burner / combustion system | Centrifugal compressor | Coupling | Positive displacement pump | VIB – Vibration | 4.2 Open circuit
Cooling tower / closed cooling circuit | Centrifugal compressor | Inlet guide vanes | Positive displacement pump | NOI – Noise | 4.3 No power / voltage
Bag filter / dust collector | Centrifugal compressor | Protection instrumentation | Positive displacement pump | OHE – Overheating | 4.4 Faulty power / voltage
Ladle & ladle / transfer car | Reciprocating compressor | Cylinders and liners | Positive displacement pump | PDE – Parameter deviation | 4.5 Earth / insulation fault
| Reciprocating compressor | Pistons and rings | Positive displacement pump | STD – Structural deficiency | 5.0 External influence – general
| Reciprocating compressor | Valves | Positive displacement pump | PLU – Plugged / choked | 5.1 Blockage / plugged
| Reciprocating compressor | Rod packing | Positive displacement pump | OTH – Other | 5.2 Contamination (process / lube oil / water)
| Reciprocating compressor | Crankshaft and bearings | Centrifugal compressor | FTS – Fail to start on demand | 5.3 Dust ingress
| Reciprocating compressor | Crosshead | Centrifugal compressor | STP – Fail to stop on demand | 5.4 Moisture / water ingress
| Reciprocating compressor | Lube system | Centrifugal compressor | UST – Spurious stop | 5.5 Heat / radiant heat / molten metal splash
| Reciprocating compressor | Pulsation dampers | Centrifugal compressor | BRD – Breakdown | 5.6 Mechanical impact / collision
| Reciprocating compressor | Cooling system | Centrifugal compressor | LOO – Low output | 6.0 Miscellaneous – general
| Reciprocating compressor | Frame / foundation | Centrifugal compressor | HIO – High output | 6.1 No cause found
| Fan / blower (incl. ID fan) | Impeller / rotor | Centrifugal compressor | ERO – Erratic output / surge | 6.2 Combined causes
| Fan / blower (incl. ID fan) | Housing | Centrifugal compressor | ELP – External leakage – process medium | 6.3 Other
| Fan / blower (incl. ID fan) | Shaft | Centrifugal compressor | ELU – External leakage – utility medium | 6.4 Unknown
| Fan / blower (incl. ID fan) | Bearings | Centrifugal compressor | INL – Internal leakage | Bearing failure (lubrication / contamination / fatigue)
| Fan / blower (incl. ID fan) | Coupling / belt drive | Centrifugal compressor | VIB – Vibration | Seal failure (dry running / wear / misalignment)
| Fan / blower (incl. ID fan) | Dampers / inlet vanes | Centrifugal compressor | NOI – Noise | Misalignment
| Fan / blower (incl. ID fan) | Foundation | Centrifugal compressor | OHE – Overheating | Unbalance
| Fan / blower (incl. ID fan) | Lubrication | Centrifugal compressor | PDE – Parameter deviation | Lubrication failure (loss / wrong / degraded lubricant)
| Electric motor | Stator winding | Centrifugal compressor | OTH – Other | Overload / operation outside design envelope
| Electric motor | Rotor | Reciprocating compressor | FTS – Fail to start on demand | Thermal cycling
| Electric motor | Bearings | Reciprocating compressor | STP – Fail to stop on demand | Scale / fouling of cooling passages
| Electric motor | Cooling fan | Reciprocating compressor | UST – Spurious stop | Slag attack / chemical attack on refractory
| Electric motor | Terminal box / cables | Reciprocating compressor | BRD – Breakdown | Abrasive wear (ore, sinter, DRI, slag)
| Electric motor | Enclosure (Ex protection) | Reciprocating compressor | LOO – Low output | Incorrect operation / operator error
| Electric motor | Anti-condensation heater | Reciprocating compressor | HIO – High output | Incorrect maintenance / reassembly
| Electric motor | Motor protection relay | Reciprocating compressor | ERO – Erratic output / surge | Design deficiency
| Gearbox | Gears | Reciprocating compressor | ELP – External leakage – process medium | Material / fabrication defect
| Gearbox | Shafts | Reciprocating compressor | ELU – External leakage – utility medium | Installation error
| Gearbox | Bearings | Reciprocating compressor | INL – Internal leakage | Ageing / end of life
| Gearbox | Seals | Reciprocating compressor | VIB – Vibration | Inadequate inspection / maintenance interval
| Gearbox | Lubrication system | Reciprocating compressor | NOI – Noise
| Gearbox | Casing | Reciprocating compressor | OHE – Overheating
| Gearbox | Couplings | Reciprocating compressor | PDE – Parameter deviation
| Belt conveyor | Belt | Reciprocating compressor | OTH – Other
| Belt conveyor | Belt splice | Fan / blower (incl. ID fan) | FTS – Fail to start on demand
| Belt conveyor | Drive pulley | Fan / blower (incl. ID fan) | STP – Fail to stop on demand
| Belt conveyor | Tail pulley | Fan / blower (incl. ID fan) | UST – Spurious stop
| Belt conveyor | Idlers | Fan / blower (incl. ID fan) | BRD – Breakdown
| Belt conveyor | Drive (motor / gearbox) | Fan / blower (incl. ID fan) | LOO – Low output
| Belt conveyor | Take-up | Fan / blower (incl. ID fan) | VIB – Vibration
| Belt conveyor | Belt scrapers | Fan / blower (incl. ID fan) | NOI – Noise
| Belt conveyor | Chutes | Fan / blower (incl. ID fan) | OHE – Overheating
| Belt conveyor | Pull-wire / belt-sway switches | Fan / blower (incl. ID fan) | STD – Structural deficiency
| Belt conveyor | Fire detection | Fan / blower (incl. ID fan) | PLU – Plugged / dust build-up
| Pressure vessel / separator / column | Shell | Fan / blower (incl. ID fan) | OTH – Other
| Pressure vessel / separator / column | Heads | Electric motor | FTS – Fail to start on demand
| Pressure vessel / separator / column | Nozzles | Electric motor | STP – Fail to stop on demand
| Pressure vessel / separator / column | Internals | Electric motor | UST – Spurious stop
| Pressure vessel / separator / column | Supports / skirt | Electric motor | BRD – Breakdown
| Pressure vessel / separator / column | Insulation | Electric motor | OHE – Overheating
| Pressure vessel / separator / column | Level instruments | Electric motor | VIB – Vibration
| Pressure vessel / separator / column | Relief device | Electric motor | NOI – Noise
| Pressure vessel / separator / column | Manway | Electric motor | PDE – Parameter deviation (high current)
| Shell & tube heat exchanger | Tubes | Electric motor | SER – Minor in-service problem
| Shell & tube heat exchanger | Tube sheet | Electric motor | OTH – Other
| Shell & tube heat exchanger | Shell | Gearbox | BRD – Breakdown
| Shell & tube heat exchanger | Channel / heads | Gearbox | VIB – Vibration
| Shell & tube heat exchanger | Gaskets | Gearbox | NOI – Noise
| Shell & tube heat exchanger | Baffles | Gearbox | OHE – Overheating
| Shell & tube heat exchanger | Supports | Gearbox | ELU – External leakage – lube oil
| Atmospheric storage tank | Shell | Gearbox | PDE – Parameter deviation
| Atmospheric storage tank | Bottom | Gearbox | STD – Structural deficiency
| Atmospheric storage tank | Roof | Gearbox | OTH – Other
| Atmospheric storage tank | Vents / PV valves | Belt conveyor | FTS – Fail to start on demand
| Atmospheric storage tank | Level gauges and alarms | Belt conveyor | UST – Spurious stop
| Atmospheric storage tank | Bund | Belt conveyor | BRD – Breakdown
| Atmospheric storage tank | Nozzles | Belt conveyor | STD – Belt tear / damage
| Atmospheric storage tank | Heating coils | Belt conveyor | PDE – Belt mistracking / misalignment
| Atmospheric storage tank | Foundation | Belt conveyor | SLP – Belt slippage
| Piping, flanges & hoses | Pipe | Belt conveyor | PLU – Chute blockage
| Piping, flanges & hoses | Flanges and gaskets | Belt conveyor | OHE – Overheating / belt fire
| Piping, flanges & hoses | Fittings | Belt conveyor | OTH – Spillage
| Piping, flanges & hoses | Supports | Belt conveyor | VIB – Vibration
| Piping, flanges & hoses | Expansion joints / bellows | Belt conveyor | NOI – Noise
| Piping, flanges & hoses | Hoses | Pressure vessel / separator / column | ELP – External leakage – process medium
| Piping, flanges & hoses | Insulation / tracing | Pressure vessel / separator / column | INL – Internal failure (internals)
| Control valve | Body | Pressure vessel / separator / column | STD – Structural deficiency
| Control valve | Trim (plug / seat) | Pressure vessel / separator / column | PLU – Plugged / fouled
| Control valve | Stem and packing | Pressure vessel / separator / column | PDE – Parameter deviation (level / pressure)
| Control valve | Actuator | Pressure vessel / separator / column | AIR – Abnormal instrument reading
| Control valve | Positioner | Pressure vessel / separator / column | OTH – Other
| Control valve | Solenoid valve | Shell & tube heat exchanger | ELP – External leakage – process medium
| Control valve | Air supply | Shell & tube heat exchanger | ELU – External leakage – utility medium
| Control valve | Limit switches | Shell & tube heat exchanger | INL – Internal leakage (tube leak)
| Isolation / ESD valve | Body | Shell & tube heat exchanger | PLU – Plugged / fouled
| Isolation / ESD valve | Ball / gate / disc | Shell & tube heat exchanger | PDE – Reduced heat transfer
| Isolation / ESD valve | Seats | Shell & tube heat exchanger | STD – Structural deficiency
| Isolation / ESD valve | Stem and packing | Shell & tube heat exchanger | OTH – Other
| Isolation / ESD valve | Actuator | Atmospheric storage tank | ELP – External leakage – process medium
| Isolation / ESD valve | Solenoid valve | Atmospheric storage tank | STD – Structural deficiency
| Isolation / ESD valve | Limit switches | Atmospheric storage tank | PDE – Overfill
| Isolation / ESD valve | Handwheel / gearbox | Atmospheric storage tank | STD – Vacuum / pressure collapse
| Pressure relief device (PSV / rupture disc) | Body | Atmospheric storage tank | PLU – Vent blocked
| Pressure relief device (PSV / rupture disc) | Nozzle and disc | Atmospheric storage tank | AIR – Abnormal level reading
| Pressure relief device (PSV / rupture disc) | Spring | Atmospheric storage tank | OTH – Other
| Pressure relief device (PSV / rupture disc) | Bellows | Piping, flanges & hoses | ELP – External leakage – process medium
| Pressure relief device (PSV / rupture disc) | Inlet / outlet piping | Piping, flanges & hoses | PLU – Plugged / choked
| Pressure relief device (PSV / rupture disc) | Rupture disc | Piping, flanges & hoses | STD – Structural deficiency
| Pressure relief device (PSV / rupture disc) | Isolation valves (locked open) | Piping, flanges & hoses | VIB – Vibration
| Instrument – transmitter / switch | Sensing element | Piping, flanges & hoses | OTH – Other
| Instrument – transmitter / switch | Transmitter electronics | Control valve | FTO – Fail to open on demand
| Instrument – transmitter / switch | Impulse lines / process connection | Control valve | FTC – Fail to close on demand
| Instrument – transmitter / switch | Cabling and junction box | Control valve | ERO – Erratic output / hunting
| Instrument – transmitter / switch | Power supply | Control valve | DOP – Delayed operation
| Instrument – transmitter / switch | Calibration | Control valve | LCP – Leakage in closed position
| Analyser / gas detector | Sensor | Control valve | ELP – External leakage – process medium
| Analyser / gas detector | Sample system | Control valve | SPO – Spurious operation
| Analyser / gas detector | Electronics | Control valve | PLU – Plugged / choked
| Analyser / gas detector | Calibration gas | Control valve | STD – Structural deficiency
| Analyser / gas detector | Housing | Control valve | AIR – Abnormal position indication
| Control system / SIS logic solver | CPU | Control valve | OTH – Other
| Control system / SIS logic solver | I/O cards | Isolation / ESD valve | FTO – Fail to open on demand
| Control system / SIS logic solver | Power supplies | Isolation / ESD valve | FTC – Fail to close on demand
| Control system / SIS logic solver | Network / communications | Isolation / ESD valve | DOP – Delayed operation
| Control system / SIS logic solver | Application software | Isolation / ESD valve | LCP – Leakage in closed position
| Control system / SIS logic solver | HMI / operator station | Isolation / ESD valve | ELP – External leakage – process medium
| Transformer | Windings | Isolation / ESD valve | SPO – Spurious operation
| Transformer | Core | Isolation / ESD valve | PLU – Plugged / choked
| Transformer | Bushings | Isolation / ESD valve | STD – Structural deficiency
| Transformer | Tap changer | Isolation / ESD valve | OTH – Other
| Transformer | Cooling (oil / fans) | Pressure relief device (PSV / rupture disc) | FTO – Fail to open on demand
| Transformer | Insulating oil | Pressure relief device (PSV / rupture disc) | PDE – Opens above set pressure
| Transformer | Protection (Buchholz / temperature) | Pressure relief device (PSV / rupture disc) | SPO – Spurious / premature opening
| Switchgear / MCC / circuit breaker | Circuit breaker | Pressure relief device (PSV / rupture disc) | LCP – Leakage through / simmering
| Switchgear / MCC / circuit breaker | Contactors | Pressure relief device (PSV / rupture disc) | FTC – Fail to reseat
| Switchgear / MCC / circuit breaker | Busbars | Pressure relief device (PSV / rupture disc) | PLU – Plugged inlet / outlet
| Switchgear / MCC / circuit breaker | Protection relays | Pressure relief device (PSV / rupture disc) | OTH – Other
| Switchgear / MCC / circuit breaker | Cables / terminations | Instrument – transmitter / switch | FTF – Fail to function on demand
| Switchgear / MCC / circuit breaker | Control circuit | Instrument – transmitter / switch | SPO – Spurious operation / false trip
| Switchgear / MCC / circuit breaker | Earthing | Instrument – transmitter / switch | AIR – Abnormal instrument reading
| Variable speed drive / UPS | Rectifier | Instrument – transmitter / switch | HIO – High reading / drift high
| Variable speed drive / UPS | DC bus capacitors | Instrument – transmitter / switch | LOO – Low reading / drift low
| Variable speed drive / UPS | Inverter / IGBTs | Instrument – transmitter / switch | NOO – No output / signal
| Variable speed drive / UPS | Cooling fans | Instrument – transmitter / switch | ERO – Erratic output
| Variable speed drive / UPS | Control board | Instrument – transmitter / switch | OTH – Other
| Variable speed drive / UPS | Batteries (UPS) | Analyser / gas detector | FTF – Fail to function on demand
| Variable speed drive / UPS | Bypass | Analyser / gas detector | SPO – Spurious operation / false trip
| Hydraulic power unit / system | Hydraulic pumps | Analyser / gas detector | AIR – Abnormal instrument reading
| Hydraulic power unit / system | Reservoir | Analyser / gas detector | HIO – High reading / drift high
| Hydraulic power unit / system | Accumulators | Analyser / gas detector | LOO – Low reading / drift low
| Hydraulic power unit / system | Directional / proportional valves | Analyser / gas detector | NOO – No output / signal
| Hydraulic power unit / system | Cylinders | Analyser / gas detector | ERO – Erratic output
| Hydraulic power unit / system | Hoses | Analyser / gas detector | OTH – Other
| Hydraulic power unit / system | Filters | Control system / SIS logic solver | FTF – Fail to function on demand
| Hydraulic power unit / system | Oil cooler | Control system / SIS logic solver | SPO – Spurious operation / false trip
| Hydraulic power unit / system | Hydraulic fluid | Control system / SIS logic solver | BRD – Loss of control
| Overhead crane / hoist (incl. ladle crane) | Hoist ropes | Control system / SIS logic solver | OTH – Loss of view (HMI)
| Overhead crane / hoist (incl. ladle crane) | Hook and block | Control system / SIS logic solver | OTH – Software / configuration error
| Overhead crane / hoist (incl. ladle crane) | Hoist brakes (primary / emergency) | Transformer | BRD – Breakdown / insulation failure
| Overhead crane / hoist (incl. ladle crane) | Gearbox / drum | Transformer | OHE – Overheating
| Overhead crane / hoist (incl. ladle crane) | Travel drives | Transformer | ELU – External leakage – insulating oil
| Overhead crane / hoist (incl. ladle crane) | Limit switches | Transformer | FOV – Faulty output voltage
| Overhead crane / hoist (incl. ladle crane) | Overload / load cell | Transformer | NOI – Noise
| Overhead crane / hoist (incl. ladle crane) | Girders / structure | Transformer | OTH – Other
| Overhead crane / hoist (incl. ladle crane) | Rails and end stops | Switchgear / MCC / circuit breaker | FTO – Fail to open / trip on demand
| Overhead crane / hoist (incl. ladle crane) | Controls / radio remote | Switchgear / MCC / circuit breaker | FTC – Fail to close on demand
| Overhead crane / hoist (incl. ladle crane) | Power supply (festoon / conductor bar) | Switchgear / MCC / circuit breaker | SPO – Spurious trip
| Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Panel pipes / copper element | Switchgear / MCC / circuit breaker | OHE – Overheating (hot joint)
| Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Inlet / outlet hoses | Switchgear / MCC / circuit breaker | BRD – Short circuit / arc flash
| Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Manifolds | Switchgear / MCC / circuit breaker | OTH – Other
| Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Flow and temperature instruments | Variable speed drive / UPS | FTS – Fail to start on demand
| Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Leak detection system | Variable speed drive / UPS | UST – Spurious stop
| Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Supports | Variable speed drive / UPS | BRD – Breakdown
| Refractory lining (furnace, ladle, tundish, kiln) | Working lining | Variable speed drive / UPS | FOV – Faulty output voltage / frequency
| Refractory lining (furnace, ladle, tundish, kiln) | Safety / permanent lining | Variable speed drive / UPS | OHE – Overheating
| Refractory lining (furnace, ladle, tundish, kiln) | Taphole / nozzle / well block | Variable speed drive / UPS | SPO – Spurious operation
| Refractory lining (furnace, ladle, tundish, kiln) | Purging plug | Variable speed drive / UPS | OTH – Other
| Refractory lining (furnace, ladle, tundish, kiln) | Anchors | Hydraulic power unit / system | LOO – Low pressure / output
| Refractory lining (furnace, ladle, tundish, kiln) | Shell | Hydraulic power unit / system | ELU – External leakage – hydraulic oil
| Burner / combustion system | Burner nozzle | Hydraulic power unit / system | BRD – Breakdown
| Burner / combustion system | Igniter | Hydraulic power unit / system | OHE – Overheating
| Burner / combustion system | Flame scanner | Hydraulic power unit / system | ERO – Erratic operation
| Burner / combustion system | Fuel train valves (double block & bleed) | Hydraulic power unit / system | SPO – Uncontrolled movement
| Burner / combustion system | Combustion air fan / damper | Hydraulic power unit / system | PLU – Filter blocked
| Burner / combustion system | Burner management system (BMS) | Hydraulic power unit / system | OTH – Other
| Burner / combustion system | Pressure switches | Overhead crane / hoist (incl. ladle crane) | Load drop / failure to hold load
| Cooling tower / closed cooling circuit | Fans and drives | Overhead crane / hoist (incl. ladle crane) | Overtravel / failure to stop
| Cooling tower / closed cooling circuit | Fill / packing | Overhead crane / hoist (incl. ladle crane) | Stoppage with load suspended
| Cooling tower / closed cooling circuit | Basin | Overhead crane / hoist (incl. ladle crane) | Uncontrolled movement
| Cooling tower / closed cooling circuit | Circulation pumps | Overhead crane / hoist (incl. ladle crane) | Structural crack / deformation
| Cooling tower / closed cooling circuit | Water treatment / dosing | Overhead crane / hoist (incl. ladle crane) | Collision
| Cooling tower / closed cooling circuit | Drift eliminators | Overhead crane / hoist (incl. ladle crane) | OTH – Other
| Cooling tower / closed cooling circuit | Plate heat exchanger | Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Water leak into furnace / vessel
| Bag filter / dust collector | Filter bags | Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Low / no cooling flow
| Bag filter / dust collector | Cages | Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Overheating / hot spot
| Bag filter / dust collector | Pulse-jet cleaning valves | Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Cracking / burn-through
| Bag filter / dust collector | Hopper and rotary valve | Water-cooled element (panel, roof, lance, tuyere, stave, mould) | Leak detection fails to alarm
| Bag filter / dust collector | Housing | Water-cooled element (panel, roof, lance, tuyere, stave, mould) | OTH – Other
| Bag filter / dust collector | Explosion vents / isolation | Refractory lining (furnace, ladle, tundish, kiln) | Excessive wear / thinning
| Bag filter / dust collector | Differential pressure instruments | Refractory lining (furnace, ladle, tundish, kiln) | Spalling / cracking
| Ladle & ladle / transfer car | Ladle shell and trunnions | Refractory lining (furnace, ladle, tundish, kiln) | Breakout / burn-through
| Ladle & ladle / transfer car | Slide gate | Refractory lining (furnace, ladle, tundish, kiln) | Hot spot on shell
| Ladle & ladle / transfer car | Porous plug | Refractory lining (furnace, ladle, tundish, kiln) | Moisture in lining
| Ladle & ladle / transfer car | Car wheels and rails | Refractory lining (furnace, ladle, tundish, kiln) | OTH – Other
| Ladle & ladle / transfer car | Car drive | Burner / combustion system | FTS – Fail to ignite
| Ladle & ladle / transfer car | Tilting mechanism | Burner / combustion system | UST – Flame failure / flame-out
| Ladle & ladle / transfer car | Power cable / festoon | Burner / combustion system | FTC – Fail to shut off fuel
|  |  | Burner / combustion system | PDE – Incorrect air / fuel ratio
|  |  | Burner / combustion system | OTH – Flashback / backfire
|  |  | Burner / combustion system | ELP – Fuel gas leakage
|  |  | Burner / combustion system | OTH – Other
|  |  | Cooling tower / closed cooling circuit | LOO – Insufficient cooling
|  |  | Cooling tower / closed cooling circuit | PLU – Fouling / scaling
|  |  | Cooling tower / closed cooling circuit | ELP – Water leakage
|  |  | Cooling tower / closed cooling circuit | VIB – Fan vibration
|  |  | Cooling tower / closed cooling circuit | PDE – Water chemistry out of specification
|  |  | Cooling tower / closed cooling circuit | STD – Structural deficiency
|  |  | Cooling tower / closed cooling circuit | OTH – Other
|  |  | Bag filter / dust collector | PLU – High differential pressure / bag blinding
|  |  | Bag filter / dust collector | ELP – Bag rupture – dust emission
|  |  | Bag filter / dust collector | OTH – Fire / explosion
|  |  | Bag filter / dust collector | PLU – Hopper blockage
|  |  | Bag filter / dust collector | FTF – Cleaning system failure
|  |  | Bag filter / dust collector | OTH – Other
|  |  | Ladle & ladle / transfer car | STD – Trunnion / shell crack
|  |  | Ladle & ladle / transfer car | FTC – Slide gate fails to close
|  |  | Ladle & ladle / transfer car | LCP – Slide gate leakage
|  |  | Ladle & ladle / transfer car | FTS – Car fails to travel
|  |  | Ladle & ladle / transfer car | OTH – Derailment / collision
|  |  | Ladle & ladle / transfer car | BRD – Breakout
|  |  | Ladle & ladle / transfer car | OTH – Other

## Rating Scales
RATING SCALES
Typical process-plant scales – calibrate Occurrence with site failure history / reliability data and align Severity with the HAZOP risk matrix before the study.
| Severity (S) | Rank | Criteria
| 10 – Hazardous – without warning | Hazardous – without warning | Failure can cause fatality, major fire / explosion or major environmental release without warning
| 9 – Hazardous – with warning | Hazardous – with warning | Failure can cause fatality, serious injury or major release, with some warning
| 8 – Very high | Very high | Loss of primary function; plant / unit shutdown > 1 week or major equipment damage
| 7 – High | High | Loss of function; unit shutdown or major production loss of several days
| 6 – Moderate | Moderate | Partial loss of function; reduced throughput or quality; significant repair cost
| 5 – Low | Low | Reduced performance; repair without shutdown at notable cost; minor reportable incident
| 4 – Very low | Very low | Minor performance degradation noticed by operators; routine repair
| 3 – Minor | Minor | Minor effect on performance; repair at next opportunity
| 2 – Very minor | Very minor | Negligible effect; cosmetic or nuisance
| 1 – None | None | No discernible effect
| Occurrence (O) | Rank | Criteria
| 10 – Very high | Very high | More than once per month
| 9 – Very high | Very high | Once per 1–3 months
| 8 – High | High | Once per 3–6 months
| 7 – High | High | Once per 6–12 months
| 6 – Moderate | Moderate | Once per 1–2 years
| 5 – Moderate | Moderate | Once per 2–5 years
| 4 – Low | Low | Once per 5–10 years
| 3 – Low | Low | Once per 10–20 years
| 2 – Remote | Remote | Once per 20–50 years
| 1 – Extremely remote | Extremely remote | Less than once per 50 years
| Detection (D) | Rank | Criteria
| 10 – Absolute uncertainty | Absolute uncertainty | Hidden failure – no means of detection before demand / functional failure
| 9 – Very remote | Very remote | Detected only after functional failure has occurred
| 8 – Remote | Remote | Detected only at proof test or shutdown inspection
| 7 – Very low | Very low | Detected only by operator senses (sight, sound, smell) on rounds
| 6 – Low | Low | Periodic inspection with limited ability to detect the failure mechanism
| 5 – Moderate | Moderate | Periodic condition monitoring (e.g. quarterly) or instrumented operator rounds
| 4 – Moderately high | Moderately high | Frequent condition monitoring (e.g. monthly) with good detection capability
| 3 – High | High | Online monitoring with alarm; detection with time to act
| 2 – Very high | Very high | Online monitoring with alarm and automatic protection; early detection
| 1 – Almost certain | Almost certain | Failure mechanism prevented or detected continuously well before functional failure
| Action thresholds (editable) | Value | Meaning
| Severity threshold | 9 | Action required for any failure mode with S at or above this value
| RPN threshold | 125 | Action required for any failure mode with RPN at or above this value
| Action Priority | H | Action required for every failure mode with Action Priority H (and justify M items left without action)
ACTION PRIORITY (AP) TABLE
Based on the AIAG-VDA FMEA Handbook (2019) Action Priority logic. Editable – verify against your licensed copy / company standard.
| Severity band | Occurrence band | Detection band → | D 7–10 | D 5–6 | D 2–4 | D 1
| S 9–10 | O 8–10 |  | H | H | H | H
| S 9–10 | O 6–7 |  | H | H | H | H
| S 9–10 | O 4–5 |  | H | H | H | M
| S 9–10 | O 2–3 |  | H | M | L | L
| S 9–10 | O 1 |  | L | L | L | L
| S 7–8 | O 8–10 |  | H | H | H | H
| S 7–8 | O 6–7 |  | H | H | H | M
| S 7–8 | O 4–5 |  | H | M | M | M
| S 7–8 | O 2–3 |  | M | M | L | L
| S 7–8 | O 1 |  | L | L | L | L
| S 4–6 | O 8–10 |  | H | H | M | M
| S 4–6 | O 6–7 |  | M | M | M | L
| S 4–6 | O 4–5 |  | M | L | L | L
| S 4–6 | O 2–3 |  | L | L | L | L
| S 4–6 | O 1 |  | L | L | L | L
| S 2–3 | O 8–10 |  | M | M | L | L
| S 2–3 | O 6–7 |  | L | L | L | L
| S 2–3 | O 4–5 |  | L | L | L | L
| S 2–3 | O 2–3 |  | L | L | L | L
| S 2–3 | O 1 |  | L | L | L | L
| S 1 | O 8–10 |  | L | L | L | L
| S 1 | O 6–7 |  | L | L | L | L
| S 1 | O 4–5 |  | L | L | L | L
| S 1 | O 2–3 |  | L | L | L | L
| S 1 | O 1 |  | L | L | L | L
Band lower limits (used by the AP look-up – keep in descending band order as in the table above)
| S band lower limits |  |  | 9 | 7 | 4 | 2 | 1
| O band lower limits |  |  | 8 | 6 | 4 | 2 | 1
| D band lower limits |  |  | 7 | 5 | 2 | 1

## Summary
FMECA SUMMARY
Counts per system worksheet (calculated).
Worksheet | System | Failure modes | AP – High | AP – Medium | AP – Low | Highest RPN | Actions required | Actions without owner | AP High after action
System 01
System 02
System 03
System 04
System 05
System 06
System 07
System 08
System 09
System 10
TOTAL
Add rows here if you copy further System worksheets.

## System 01
FMECA WORKSHEET
Select system ▸ |  |  | S01 – Gas receiving & metering station (GRMS) | [6 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments
| ESDV-1001 |  | Actuator | Close on ESD demand | FTC – Fail to close on demand | 1.6 Sticking / seizure | 5.3 Dust ingress | Inadequate inspection / maintenance interval |  | Inlet not isolated | Release in the GRMS / PRS keeps being fed from the pipeline | Prolonged jet fire / larger vapour cloud (ETA-GN-01 H2) | 9 – Hazardous – with warning | Annual full-stroke test | 3 – Low | Proof test / function test | 6 – Low |  |  |  | Six-monthly partial-stroke test between annual full-stroke tests (R-001) | Failure-finding / proof test | Instrument engineer | 2027-03-31 | 9 – Hazardous – with warning | 3 – Low | 4 – Moderately high |  |  | HAZOP N01-05 | Fault tree FT-GN-02 event ESDV-1001
| PR-1001 |  | Manway | Contain pressure; open only when depressurised | ELP – External leakage – process medium | Incorrect operation / operator error | 1.1 Leakage |  |  | Closure opened / leaking under pressure | Gas release at the GRMS | Injury to the operator; fire (BT-GN-01 T5) | 10 – Hazardous – without warning | Pigging procedure OP-GN-010 | 3 – Low | None – failure evident only on occurrence | 9 – Very remote |  |  |  | Verify the pressure-warning / key-interlock device and train pigging crews (R-017) | Redesign / modification (MOC) | Mechanical engineer | 2027-03-31 | 10 – Hazardous – without warning | 2 – Remote | 4 – Moderately high |  |  | HAZOP N01-07
| F-1002A |  | Internals | Remove liquids and solids | PLU – Plugged / fouled | 5.1 Blockage / plugged | 5.2 Contamination (process / lube oil / water) |  |  | High differential pressure | Change-over to F-1002B; carry-over to regulators if not acted on | Active regulator may stick open (FT-GN-01 initiating cause) | 6 – Moderate | Duty / standby; element change on dP | 5 – Moderate | Performance monitoring (flow, ΔP, efficiency) | 3 – High | [12 empty] | HAZOP N01-03
| FT-1003A |  | Transmitter electronics | Measure custody flow | AIR – Abnormal instrument reading | 3.4 Out of adjustment / calibration drift |  |  |  | Meter error | Custody-transfer dispute | Commercial only | 3 – Minor | Annual verification | 4 – Low | Calibration check | 3 – High | [12 empty] | HAZOP N01-01
| PSV-1006A |  | Nozzle and disc | Relieve fire / thermal overpressure | FTO – Fail to open on demand | 2.2 Corrosion (general / pitting / CUI) | 5.1 Blockage / plugged |  |  | No relief | Filter-separator overpressure in a fire | Vessel rupture in a fire | 8 – Very high | Bench test every 4 years | 2 – Remote | Proof test / function test | 7 – Very low |  |  |  | Reduce the bench-test interval to 2 years (fire-case relief only protection) | Failure-finding / proof test | Mechanical engineer | 2027-03-31 | 8 – Very high | 2 – Remote | 5 – Moderate |  |  | HAZOP N01-02

## System 02
FMECA WORKSHEET
Select system ▸ |  |  | S02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | [6 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments
| PCV-1104A |  | Trim (plug / seat) | Control PRS outlet at 7.0 barg | FTC – Fail to close on demand | 5.2 Contamination (process / lube oil / water) | 5.4 Moisture / water ingress | 1.6 Sticking / seizure |  | Active regulator fails open | Monitor regulator must take over (demand on protection) | If monitor and slam-shut also fail – MP network overpressure (HAZOP N02-02) | 9 – Hazardous – with warning | Pilot filter; heater keeps outlet ≥ 5 °C | 5 – Moderate | Process alarm (DCS) | 3 – High |  |  |  | Pilot supply filter change and heater outlet temperature alarm (R-004) | Time-based maintenance / overhaul | Instrument engineer | 2027-03-31 | 9 – Hazardous – with warning | 4 – Low | 3 – High |  |  | HAZOP N02-02 | Initiating event in fault tree FT-GN-01 (BE-001)
| PCV-1103A |  | Positioner | Take over at 7.5 barg if the active regulator fails open | FTC – Fail to close on demand | 1.6 Sticking / seizure | 3.4 Out of adjustment / calibration drift |  |  | Monitor does not take over | Only the slam-shut remains | MP network overpressure if the slam-shut also fails | 10 – Hazardous – without warning | Set-point check at overhaul | 3 – Low | Proof test / function test | 7 – Very low |  |  |  | Annual lock-up and take-over test of the monitor regulators (R-003) | Failure-finding / proof test | Instrument engineer | 2027-03-31 | 10 – Hazardous – without warning | 3 – Low | 4 – Moderately high |  |  | HAZOP N02-02 | Fault tree FT-GN-01 events BE-004 / BE-005
| SSV-1102A |  | Actuator | Close run A at 8.5 barg (OPSO) | FTC – Fail to close on demand | 1.6 Sticking / seizure | 3.4 Out of adjustment / calibration drift | Incorrect maintenance / reassembly |  | Slam-shut does not trip | No shut-off if the monitor has also failed | MP network overpressure | 10 – Hazardous – without warning | Trip test at overhaul | 3 – Low | Proof test / function test | 7 – Very low |  |  |  | Six-monthly trip test with a calibrated test rig (R-003) | Failure-finding / proof test | Instrument engineer | 2027-03-31 | 10 – Hazardous – without warning | 3 – Low | 4 – Moderately high |  |  | HAZOP N02-02 | Fault tree FT-GN-01 events BE-006 / BE-007 / BE-008
| SSV-1102A |  | Solenoid valve | Stay open in normal operation | SPO – Spurious operation | 3.4 Out of adjustment / calibration drift | 1.2 Vibration |  |  | Run A closes | Run B takes over (set 0.3 bar lower) | If run B fails – low header pressure, flame-outs (HAZOP N02-03) | 6 – Moderate | Run B on automatic | 4 – Low | Process alarm (DCS) | 2 – Very high | [12 empty] | HAZOP N02-03
| H-1101A |  | Burner management system (BMS) | Keep the bath at temperature; trip safely | UST – Flame failure / flame-out | 3.1 Control failure | 5.2 Contamination (process / lube oil / water) |  |  | Heater trips | Gas outlet temperature falls | Ice / hydrate in regulator pilots; MDMT (HAZOP N02-01) | 6 – Moderate | Duty / standby heaters | 5 – Moderate | Process alarm (DCS) | 3 – High |  |  |  | Automatic change-over to H-1101B on heater trip (R-004) | Redesign / modification (MOC) | Process engineer | 2027-03-31 | 6 – Moderate | 3 – Low | 3 – High |  |  | HAZOP N02-01
| TT-1101 |  | Sensing element | Measure gas outlet temperature | HIO – High reading / drift high | 3.4 Out of adjustment / calibration drift |  |  |  | Reads high | TIC under-heats; TSL-1101 does not alarm | Low gas temperature undetected (HAZOP N02-01) | 6 – Moderate | Annual calibration | 3 – Low | Calibration check | 5 – Moderate | [12 empty] | HAZOP N02-01

## System 03
FMECA WORKSHEET
Select system ▸ |  |  | S03 – MP ring main (7 barg) and pipe racks | [6 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments
| L-1200 |  | Pipe | Contain 7 barg gas | ELP – External leakage – process medium | 2.2 Corrosion (general / pitting / CUI) | 5.6 Mechanical impact / collision |  |  | Leak from the ring main | Gas release in a plant area | Fire / explosion (BT-GN-01 T2, T3) | 10 – Hazardous – without warning | Coating + CP; crash barriers | 3 – Low | Ultrasonic thickness / NDT inspection | 5 – Moderate |  |  |  | UT at supports and crossings every 2 years; review crash protection (R-009) | Condition monitoring task | Inspection engineer | 2027-03-31 | 10 – Hazardous – without warning | 2 – Remote | 4 – Moderately high |  |  | HAZOP N03-01
| L-1200 |  | Flanges and gaskets | Contain 7 barg gas | ELP – External leakage – process medium | Installation error | 1.2 Vibration |  |  | Flange leak | Gas release on the rack | Fire / explosion (BT-GN-01 T4) | 9 – Hazardous – with warning | Gasket specification | 4 – Low | Operator rounds – visual / sensory | 6 – Low |  |  |  | Bolt-torque procedure and annual acoustic leak survey | Condition monitoring task | Maintenance planner | 2027-03-31 | 9 – Hazardous – with warning | 3 – Low | 3 – High |  |  | HAZOP N03-01
| CP-1200 |  | Windings | Supply CP current | FOV – Faulty output voltage | 4.3 No power / voltage | Ageing / end of life |  |  | No / low CP current | Buried sections unprotected | Accelerated external corrosion – leak (HAZOP N03-04) | 7 – High | Annual CP survey | 4 – Low | Performance monitoring (flow, ΔP, efficiency) | 6 – Low |  |  |  | Monthly transformer-rectifier readings with alarm on low output | Operator round / inspection | Electrical engineer | 2027-03-31 | 7 – High | 4 – Low | 3 – High |  |  | HAZOP N03-04
| XV-1201 |  | Actuator | Close for sectional isolation | FTC – Fail to close on demand | 1.6 Sticking / seizure |  |  |  | Section cannot be isolated remotely | Larger inventory released | Longer release duration | 7 – High | None | 3 – Low | Proof test / function test | 7 – Very low |  |  |  | Annual stroke test of sectionalising valves | Failure-finding / proof test | Instrument engineer | 2027-03-31 | 7 – High | 3 – Low | 4 – Moderately high |  |  | HAZOP N03-01

## System 04
FMECA WORKSHEET
Select system ▸ |  |  | S04 – DRI plant gas supply – district station DS-2 | [6 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments
| FCV-2004 |  | Positioner | Control reformer fuel flow | FTC – Fail to close on demand | 3.1 Control failure | 1.6 Sticking / seizure |  |  | Valve fails open | Reformer over-firing | Tube overheating / rupture (HAZOP N04-01) | 8 – Very high | Reformer BMS high-fuel / tube-temperature trips | 3 – Low | Protective trip / interlock | 3 – High | [12 empty] | HAZOP N04-01
| XV-2008 |  | Ball / gate / disc | Shut tight against reverse flow | LCP – Leakage in closed position | 2.3 Erosion | 5.2 Contamination (process / lube oil / water) |  |  | Passing valve | Process gas back-flows into NG when NG pressure is low | CO / H2 in the NG system (HAZOP N04-03) | 9 – Hazardous – with warning | Double NRV | 3 – Low | None – hidden failure | 8 – Remote |  |  |  | Annual reverse-flow leak test of XV-2008 and the NRVs (R-018) | Failure-finding / proof test | DRI maintenance | 2027-03-31 | 9 – Hazardous – with warning | 3 – Low | 4 – Moderately high |  |  | HAZOP N04-03
| PSLL-2006 |  | Sensing element | Trip reformer burners on low gas pressure | FTF – Fail to function on demand | 3.4 Out of adjustment / calibration drift | 5.1 Blockage / plugged |  |  | No trip | Reformer burners not tripped on gas loss | Relight hazard (HAZOP N04-02) | 8 – Very high | Annual proof test | 3 – Low | Proof test / function test | 7 – Very low | [12 empty] | HAZOP N04-02

## System 05
FMECA WORKSHEET
Select system ▸ |  |  | S05 – Melt shop gas supply – DS-3, EAF oxy-fuel burners and ladle preheaters | [6 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments
| NRV-3010 |  | Seats | Prevent O2 back-flow into NG | LCP – Leakage in closed position | 5.1 Blockage / plugged | 5.5 Heat / radiant heat / molten metal splash |  |  | Check valve passing | O2 can enter the NG line when NG pressure is lost | Flashback / detonation in the burner line (HAZOP N05-01) | 10 – Hazardous – without warning | Flashback arrestor in series | 3 – Low | None – hidden failure | 8 – Remote |  |  |  | Annual back-flow test of NRVs; prove the 'low NG closes O2' interlock (R-013) | Failure-finding / proof test | Melt shop maintenance | 2027-03-31 | 10 – Hazardous – without warning | 3 – Low | 4 – Moderately high |  |  | HAZOP N05-01
| XV-3011 |  | Solenoid valve | Shut off NG to the burner on trip | FTC – Fail to close on demand | 5.3 Dust ingress | 5.5 Heat / radiant heat / molten metal splash |  |  | NG not shut off | Burner keeps flowing gas after a trip | Gas accumulation / fire at the EAF (HAZOP N05-02) | 9 – Hazardous – with warning | Annual function test | 3 – Low | Proof test / function test | 6 – Low |  |  |  | Heat-shield the valve and test six-monthly (R-019) | Failure-finding / proof test | Melt shop maintenance | 2027-03-31 | 9 – Hazardous – with warning | 3 – Low | 4 – Moderately high |  |  | HAZOP N05-02
| LPH-3020 |  | Flame scanner | Detect loss of flame | FTC – Fail to shut off fuel | 3.3 Faulty signal / indication / alarm | 5.3 Dust ingress |  |  | Flame loss not detected | Gas keeps flowing into the ladle | Explosion on relight (HAZOP N05-03) | 10 – Hazardous – without warning | Self-checking UV scanner | 3 – Low | Proof test / function test | 6 – Low | [12 empty] | HAZOP N05-03

## System 06
FMECA WORKSHEET
Select system ▸ |  |  | S06 – Rolling-mill reheat furnace fuel gas train and burner management | [6 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments
| BS-4010 |  | Sensing element | Detect loss of flame within 1 s | FTF – Fail to function on demand | 3.3 Faulty signal / indication / alarm | 5.3 Dust ingress | 5.5 Heat / radiant heat / molten metal splash |  | Scanner keeps reporting flame | BMS does not shut off fuel | Explosive mixture in the furnace (FT-GN-03, ETA-GN-02) | 10 – Hazardous – without warning | Annual scanner check | 4 – Low | Proof test / function test | 6 – Low |  |  |  | Self-checking UV scanners, 1oo2 per burner; six-monthly test (R-010) | Redesign / modification (MOC) | Instrument engineer | 2027-03-31 | 10 – Hazardous – without warning | 2 – Remote | 4 – Moderately high |  |  | HAZOP N06-01 | Fault tree FT-GN-03 event BE-003
| XV-4002A |  | Actuator | Close within 1 s on trip | FTC – Fail to close on demand | 1.6 Sticking / seizure | 5.2 Contamination (process / lube oil / water) |  |  | SSOV A does not close | SSOV B must close (1oo2); common cause can fail both | Explosive mixture if both fail (FT-GN-03) | 10 – Hazardous – without warning | Annual function test | 3 – Low | Proof test / function test | 6 – Low |  |  |  | Measure closing time at every shutdown; staggered testing (R-010) | Failure-finding / proof test | Instrument engineer | 2027-03-31 | 10 – Hazardous – without warning | 3 – Low | 4 – Moderately high |  |  | HAZOP N06-01 | Fault tree FT-GN-03 events BE-006 / BE-007 (CCF-001)
| XV-4002A |  | Seats | Shut tight when the furnace is idle | LCP – Leakage in closed position | 2.3 Erosion | 5.2 Contamination (process / lube oil / water) |  |  | Passing valve | Gas accumulates in the idle furnace | Explosion at light-off (BT-GN-02 T2) | 10 – Hazardous – without warning | DBB vent XV-4003 | 4 – Low | Proof test / function test | 4 – Moderately high |  |  |  | Valve proving VPS-4004 before every light-off (R-011) | Failure-finding / proof test | Instrument engineer | 2027-03-31 | 10 – Hazardous – without warning | 3 – Low | 2 – Very high |  |  | HAZOP N06-05
| BMS-4000 |  | Application software | Execute purge, light-off and flame-failure logic | OTH – Software / configuration error | 3.5 Software / configuration failure |  |  |  | Logic error / unauthorised change | Trips not executed | As N06-01 / N06-04 | 10 – Hazardous – without warning | Password protection | 2 – Remote | None – hidden failure | 8 – Remote |  |  |  | Logic changes only under MOC with full function test; bypass register (R-012) | Procedure / training | Instrument engineer | 2027-03-31 | 10 – Hazardous – without warning | 2 – Remote | 5 – Moderate |  |  | HAZOP N06-06 | Fault tree FT-GN-03 event BE-005
| FN-4007 |  | Bearings | Supply combustion air | UST – Spurious stop | Bearing failure (lubrication / contamination / fatigue) |  |  |  | Fan trips | FSLL-4008 trips the furnace | Production loss; if trip fails – rich combustion (BT-GN-02 T4) | 6 – Moderate | Lubrication schedule | 4 – Low | Online vibration monitoring with alarm | 2 – Very high | [12 empty] | HAZOP N06-03

## System 07
FMECA WORKSHEET
Select system ▸ |  |  | S07 – Purge, vent, blowdown and maintenance isolation | [6 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments
| N2-1304 |  | Hoses | Purge with N2 and then be disconnected | OTH – Other | Incorrect operation / operator error |  |  |  | Hose left connected after purging | NG back-flows into the plant N2 header | Flammable gas in N2 users incl. hot DRI conveyor XS-210 (HAZOP N07-03) | 9 – Hazardous – with warning | Purge procedure | 4 – Low | None – hidden failure | 8 – Remote |  |  |  | Removable spool / hose only, check valve + DBB, disconnect after use (R-014) | Redesign / modification (MOC) | Utilities manager | 2027-03-31 | 9 – Hazardous – with warning | 2 – Remote | 4 – Moderately high |  |  | HAZOP N07-03
| BDV-1302 |  | Seats | Stay tight when closed | LCP – Leakage in closed position | 2.3 Erosion |  |  |  | Passing blowdown valve | Continuous small release at VS-1301 | Gas loss; flammable plume at the stack | 5 – Low | None | 3 – Low | Acoustic emission / ultrasonic leak detection | 4 – Moderately high | [12 empty] | HAZOP N07-04
| VS-1301 |  | Pipe | Discharge vented gas to a safe height | PLU – Plugged / choked | 5.1 Blockage / plugged |  |  |  | Stack blocked (rain cap, nest) | Back-pressure on vents / PSV-1105 | Gas vented inside the shelter | 7 – High | None | 2 – Remote | Shutdown inspection | 6 – Low | [12 empty] | HAZOP N07-04

## System 08
FMECA WORKSHEET
Select system ▸ |  |  | S08 – Gas detection, F&G and ESD system | [6 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments
| GD-1110A |  | Sensor | Detect gas at 20 % / 40 % LEL | FTF – Fail to function on demand | 3.4 Out of adjustment / calibration drift | 5.3 Dust ingress | Ageing / end of life |  | Detector does not respond | 2oo3 vote degraded; a common cause can blind all three | ESD not initiated automatically (FT-GN-02) | 9 – Hazardous – with warning | Six-monthly calibration | 4 – Low | Calibration check | 5 – Moderate |  |  |  | Quarterly bump test; sensor replacement on age (R-001) | Failure-finding / proof test | Instrument engineer | 2027-03-31 | 9 – Hazardous – with warning | 3 – Low | 3 – High |  |  | HAZOP N08-04 | Fault tree FT-GN-02 events BE-001…003, CCF-001
| UCP-1000 |  | I/O cards | Execute the ESD logic | FTF – Fail to function on demand | 4.0 Electrical failure – general |  |  |  | Output not de-energised | ESD valves not commanded closed | Release not isolated (FT-GN-02) | 10 – Hazardous – without warning | Certified SIS with diagnostics | 2 – Remote | Protective trip / interlock | 3 – High | [12 empty] | HAZOP N08-01 | Fault tree FT-GN-02 event BE-004
| UPS-1000 |  | Batteries (UPS) | Back up SIS / F&G power for 30 min | BRD – Breakdown | Ageing / end of life |  |  |  | UPS fails on mains loss | SIS de-energises – ESD valves close (fail-safe) | Total gas loss to the works (HAZOP N08-02) | 7 – High | Annual discharge test | 3 – Low | Performance monitoring (flow, ΔP, efficiency) | 3 – High | [12 empty] | HAZOP N08-02
| HS-1000 |  | Cabling and junction box | Transmit the manual ESD demand | FTF – Fail to function on demand | 4.2 Open circuit | 5.4 Moisture / water ingress |  |  | Push button circuit fails | Manual ESD unavailable | As FT-GN-02 gate G-004 | 8 – Very high | Supervised circuit | 2 – Remote | Proof test / function test | 6 – Low | [12 empty] | HAZOP N08-03 | Fault tree FT-GN-02 event BE-008

## System 09
FMECA WORKSHEET
Select system ▸ | [9 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments

## System 10
FMECA WORKSHEET
Select system ▸ | [9 empty] | Session date |  |  | Equipment items
System title
Function / performance standard
Operating context
System boundaries
P&IDs / drawings
Related HAZOP node(s)
ONE ROW PER FAILURE MODE. Pick the equipment tag (tags of the selected system), component and failure mode; pick up to 3 causes (listed line by line in 'Failure causes / mechanisms'). Rate S, O, D – RPN, Action Priority and 'Action required?' are calculated. Rate again after the recommended action. Use the [–] button above the Cause columns to collapse them.
ITEM / FAILURE MODE | [5 empty] | CAUSE PICK-LIST |  |  | CAUSES & EFFECTS |  |  |  | CRITICALITY – CURRENT | [7 empty] | RECOMMENDED ACTIONS |  |  |  | CRITICALITY – AFTER ACTION |  |  |  |  | LINKS
Ref | Equipment tag | Equipment type (auto) | Component / maintainable item | Function of item | Failure mode | Cause 1 | Cause 2 | Cause 3 | Failure causes / mechanisms | Local effect | System effect | End effect (safety / environment / production) | Severity (S) | Current prevention controls | Occurrence (O) | Current detection method | Detection (D) | RPN | AP | Action required? | Recommended action | Action / task type | Action by | Due date | Severity (S) | Occurrence (O) | Detection (D) | RPN after | AP after | HAZOP ref. | Comments