## Cover
HAZOP STUDY WORKBOOK
Hazard and Operability Study – chemical, steel & metals processes
Legend: | Yellow = enter / select data | Grey = formula (do not overwrite) | Blue = returned from another sheet
STUDY DETAILS
Study title | PHA / HAZOP – Natural gas distribution network (worked example)
Company / site | Hadeed – integrated DRI-EAF steel works (illustrative example)
Plant / unit / area | Utilities – natural gas receiving, pressure reduction and plant distribution
Project / MOC reference | PHA revalidation – plant natural gas network
Study type | HAZOP – revalidation
Document number | HZ-EX-GN-001
Revision | A
Study start date | 2026-10-12
Study end date | 2026-10-14
Venue / platform | Utilities training room
Scope of study | Natural gas from the supplier's custody-transfer battery limit through the gas receiving & metering station (GRMS), gas heaters and pressure reduction station PRS-1, the 7 barg MP ring main, the district stations and fuel trains of the DRI plant (DS-2), melt shop (DS-3) and rolling-mill reheat furnace (DS-4 / fuel train), the purge / vent / blowdown facilities, and the gas detection & ESD system protecting the network.
Exclusions | Supplier pipeline upstream of ESDV-1001; burner internals and combustion inside the DRI reformer (covered by the DRI plant HAZOP); oxygen plant and O2 distribution (except the NG/O2 interface at oxy-fuel burners); plant N2 generation.
Design basis / design intent summary | Receive natural gas at 35–42 barg (pipeline MAOP 50 barg), filter, meter and heat it, reduce it to 7 barg (MP header design 10 barg) and distribute it to the plant users at the pressure and quality they need, without loss of containment. All values are illustrative – confirm against the gas network design basis, P&IDs and relief / SIL studies.
Operating modes covered | Normal operation, start-up / re-pressurisation after supply interruption, regulator-run change-over, pigging, purging and gas-in / gas-out for maintenance, emergency shutdown
Facilitator | A. Facilitator
Scribe | B. Scribe
Risk matrix used | 5 x 5 matrix – see 'Risk Matrix' sheet
Guideword set | HAZOP Guidewords – Chemical, Steel & Metals (see 'Lists' sheet)
Number of nodes
STUDY TEAM
Name | Company | Discipline / role | Sessions / days attended | Signature
A. Facilitator | Istec | Facilitator | Days 1–3
B. Scribe | Istec | Scribe | Days 1–3
C. Gas Network | Utilities | Process engineer | Days 1–3
D. Operator | Utilities | Operations representative | Days 1–3
E. Instrument | Maintenance | Instrument / control engineer | Days 1–3
F. Mechanical | Maintenance | Mechanical engineer | Days 1–2
G. Safety | HSE | HSE / process safety | Days 1–3
H. Furnace | Rolling mill | Operations representative | Day 3
I. DRI | DRI plant | Process engineer | Day 2
APPROVAL
| Name | Position | Signature | Date
Prepared by
Reviewed by
Approved by
WORKBOOK CONTENTS
Cover | Study details, team, approval
PSI | Process safety information register – drawings, procedures, data used in the study
Nodes | Node list: name, drawings, battery limits, functional description, design and operating parameters
Lists | Drop-down sources: parameters, guidewords, potential causes, PSI categories (editable)
Risk Matrix | 5 x 5 severity x likelihood matrix (scores 1–25), descriptors and risk bands (editable)
Node 01 … Node 10 | One worksheet per node – select the node at the top; one row per cause / safeguard

## PSI
PROCESS SAFETY INFORMATION REGISTER
List every drawing, procedure and data source used by the team. Pre-filled with a typical checklist – delete or add rows as required.
Ref | Category | Document number | Title / description | Revision | Date | Owner / custodian | Status | Applicable nodes | Comments
PSI-01 | Drawings | P&ID-GN-1001 | Gas receiving & metering station (GRMS) P&ID | A |  | Utilities | Available | N01
PSI-02 | Drawings | P&ID-GN-1101 | Gas heaters and pressure reduction station PRS-1 P&ID | A |  | Utilities | Available | N02
PSI-03 | Drawings | P&ID-GN-1201/1202 | MP ring main and pipe-rack routing | A |  | Utilities | Available | N03
PSI-04 | Drawings | P&ID-GN-2001 | DRI plant district station DS-2 | A |  | Utilities | Available | N04
PSI-05 | Drawings | P&ID-GN-3001 | Melt shop district station DS-3, oxy-fuel burners and ladle preheaters | A |  | Utilities | Available | N05
PSI-06 | Drawings | P&ID-GN-4001 | Rolling-mill reheat furnace fuel gas train and BMS | A |  | Utilities | Available | N06
PSI-07 | Drawings | P&ID-GN-1301 | Vent stack, blowdown and N2 purge connections | A |  | Utilities | Available | N07
PSI-08 | Drawings | C&E-GN-1000 | ESD / F&G cause-and-effect charts | A |  | Utilities | Available | N01, N02, N08
PSI-09 | Drawings | HAC-GN-001 | Hazardous area classification – gas network | A |  | Utilities | Available | N01, N02, N03, N07
PSI-10 | Process technology | DB-GN-001 | Gas network design basis (pressures, set points, MDMT) | A |  | Utilities | Available | N01, N02, N03
PSI-11 | Equipment | RS-GN-001 | Relief and overpressure protection study | A |  | Utilities | Available | N01, N02, N07
PSI-12 | Equipment | SRS-GN-001 | Safety requirements specification – gas ESD and furnace BMS | A |  | Utilities | Available | N06, N08
PSI-13 | Hazardous materials | SDS-NG-001 | Natural gas safety data sheet; gas supply quality specification | A |  | Utilities | Available | N01
PSI-14 | Procedures | OP-GN-010 | Pigging procedure (pig receiver PR-1001) | A |  | Utilities | Available | N01, N07
PSI-15 | Procedures | OP-GN-020 | Purging and gas-in / gas-out procedure | A |  | Utilities | Available | N03, N07
PSI-16 | Procedures | OP-RM-040 | Reheat furnace light-off and shutdown procedure | A |  | Utilities | Available | N06
PSI-17 | Previous studies | HZ-GN-2019 | Previous gas network HAZOP (2019) and close-out status | A |  | Utilities | Available | N01, N02, N03
PSI-18 | Previous studies | INC-GN-LOG | Gas incident / near-miss log (last 5 years) | A |  | Utilities | Available | N03, N05, N06
PSI-19
PSI-20
PSI-21
PSI-22
PSI-23
PSI-24
PSI-25
PSI-26
PSI-27
PSI-28
PSI-29
PSI-30
PSI-31
PSI-32
PSI-33
PSI-34
PSI-35
PSI-36
PSI-37
PSI-38
PSI-39
PSI-40
PSI-41
PSI-42
PSI-43
PSI-44
PSI-45
PSI-46
PSI-47
PSI-48
PSI-49
PSI-50

## Nodes
NODE LIST
One row per node. Node title (column C) feeds the drop-down at the top of each node worksheet.
Node No. | Node name | Node title (auto) | P&IDs / drawings | Battery limits (from – to) | Functional description / design intent | Design parameters | Operating parameters | Comments
N01 | Gas receiving & metering station (GRMS) |  | P&ID-GN-1001 | From the supplier battery-limit insulating joint IJ-1001 through inlet ESD valve ESDV-1001, pig receiver PR-1001, filter-separators F-1002A/B and ultrasonic meter runs FT-1003A/B to the inlet of the gas heaters | Receive natural gas from the supplier's pipeline, remove liquids and solids and meter it for custody transfer | Design 50 barg / -10 to 60 °C (= pipeline MAOP); 2 x 100 % filter-separators; 2 x 100 % meter runs | 35–42 barg; 20–35 °C; up to 120 000 Sm3/h | Materials: Natural gas (methane > 90 %, extremely flammable, asphyxiant); traces of H2S, condensate, black powder
N02 | Gas heaters H-1101A/B and pressure reduction station PRS-1 |  | P&ID-GN-1101 | From the heater inlet through water-bath heaters H-1101A/B and regulator runs A/B (slam-shut SSV-1102, monitor PCV-1103, active PCV-1104) to outlet ESD valve ESDV-1107, incl. token relief PSV-1105 | Pre-heat the gas to offset Joule–Thomson cooling (~0.5 °C per bar) and reduce it from 35–42 barg to 7 barg without exceeding the MP design pressure | Inlet 50 barg; outlet piping 10 barg design; set points: active 7.0, monitor 7.5, SSV OPSO 8.5, PSV-1105 9.0 barg; outlet temperature ≥ 5 °C | Outlet 6.8–7.2 barg; heater outlet 30–40 °C upstream of the regulators; run A duty / run B standby (set 0.3 bar lower) | Materials: Natural gas; hot water / glycol bath; heater flue gases
N03 | MP ring main (7 barg) and pipe racks |  | P&ID-GN-1201/1202 | From ESDV-1107 around the plant ring main (24") with sectionalising valves XV-1201…1204 to the inlet isolation of each district station (DS-2, DS-3, DS-4); buried road crossings with cathodic protection CP-1200 | Distribute 7 barg gas to all plant users with sectional isolation and without loss of containment | Design 10 barg; API 5L carbon steel; buried sections coated + impressed-current CP | 6.8–7.2 barg; ambient temperature | Materials: Natural gas
N04 | DRI plant gas supply – district station DS-2 |  | P&ID-GN-2001 | From the DS-2 inlet ESDV-2001 via regulators PCV-2002A/B to the reformer fuel gas control valve FCV-2004 and the process-gas NG make-up point (XV-2008) | Supply natural gas to the DRI reformer burners (fuel) and as make-up to the reducing-gas circuit at controlled pressure and flow | Design 10 barg (full MP pressure); outlet 4.5 barg | 4.0–4.5 barg; flow on reformer firing demand | Materials: Natural gas; reducing / process gas (H2, CO – toxic, flammable) at the make-up point
N05 | Melt shop gas supply – DS-3, EAF oxy-fuel burners and ladle preheaters |  | P&ID-GN-3001 | From DS-3 inlet ESDV-3001 via PCV-3002A, slam-shut SSV-3003 and PSV-3004 to the EAF oxy-fuel burner skids (XV-3011, NRV-3010) and ladle preheaters LPH-3020 | Supply natural gas to the EAF oxy-fuel burners and ladle / tundish preheaters at controlled pressure | Design 10 barg; outlet 2.0 barg; O2 supply to burners 10 barg | 1.8–2.0 barg; intermittent firing | Materials: Natural gas; oxygen (oxidiser); molten metal / slag nearby
N06 | Rolling-mill reheat furnace fuel gas train and burner management |  | P&ID-GN-4001 | From DS-4 regulator PCV-4001 through safety shut-off valves XV-4002A/B (with vent XV-4003 and valve proving VPS-4004) to the zone burners B-4020, incl. BMS-4000, flame scanners BS-4010 and combustion air fan FN-4007 | Deliver fuel gas to the reheat furnace burners only when safe to fire (purged, air proven, flame proven) and shut it off on any unsafe condition | Design 10 barg upstream / 2 barg downstream of PCV-4001; SSOV closing time < 1 s | 0.3–1.5 barg at the burners; furnace 900–1250 °C; light-off from cold after outages | Materials: Natural gas; combustion air; flue gas (CO)
N07 | Purge, vent, blowdown and maintenance isolation |  | P&ID-GN-1301 | Vent stack VS-1301 and blowdown valve BDV-1302 at the PRS, spectacle blinds SB-1303 and N2 purge connections N2-1304 at GRMS, PRS and district stations | Allow equipment to be depressurised, purged, isolated and returned to service without creating flammable mixtures, releases or asphyxiation hazards | Vent stack 3 m above the highest platform within 15 m; N2 purge supply 8 barg | Used during maintenance, pigging and gas-in / gas-out | Materials: Natural gas; nitrogen (asphyxiant); air
N08 | Gas detection, F&G and ESD system |  | C&E-GN-1000 | Gas detectors GD-1110A/B/C (PRS shelter, 2oo3), GRMS detectors, manual ESD stations HS-1000, SIS logic solver UCP-1000 and UPS-1000, acting on ESDV-1001 / ESDV-1107 and the district-station ESD valves | Detect a gas release in the HP / MP system and isolate the gas inventory automatically or on manual demand | SIS per SRS-GN-001; ESD valves fail-closed; UPS 30 min | Normally on line; detectors 20 % / 40 % LEL alarm / trip | Materials: Natural gas
N09
N10
N11
N12
N13
N14
N15
N16
N17
N18
N19
N20
N21
N22
N23
N24
N25
N26
N27
N28
N29
N30

## Lists
DROP-DOWN LISTS
Source: HAZOP Guidewords – Chemical, Steel & Metals. To add a cause, INSERT a row inside its key block (keys must stay grouped). [C] = mainly chemical, [S] = mainly steel & metals.
Parameters | Parameter | Guideword | Key | Typical deviation (from guideword guide) | Key (parameter¦guideword) | Potential cause | Guideword | Meaning | PSI category | IPL?
Flow | Flow | NO | Flow¦NO | No flow | Flow¦NO | Empty source vessel, feed tank, bin or gas holder | NO | Complete negation of intent | Drawings | Yes
Pressure | Flow | REVERSE | Flow¦REVERSE | Reverse flow | Flow¦NO | Wrong routing / incorrect valve line-up | MORE | Quantitative increase | Process technology | No
Temperature | Flow | MORE | Flow¦MORE | More flow | Flow¦NO | Blockage, gas lock or vapour lock | LESS | Quantitative decrease | Hazardous materials
Level | Flow | LESS | Flow¦LESS | Less flow | Flow¦NO | Slip plate / spectacle blind left in or incorrectly installed | AS WELL AS | Something additional present | Equipment
Composition | Flow | OTHER THAN | Flow¦OTHER THAN | Misdirected flow (Other than – wrong destination) | Flow¦NO | Non-return valve fitted the wrong way round | PART OF | Only part of intent achieved | Procedures
Phase | Flow | AS WELL AS | Flow¦AS WELL AS | As well as (additional material or phase in the flow) | Flow¦NO | Burst pipe or large leak upstream | REVERSE | Logical opposite | Previous studies
Reaction | Pressure | MORE | Pressure¦MORE | More pressure | Flow¦NO | Equipment failure – control valve fails closed, isolation valve, pump or compressor trip, vessel failure | OTHER THAN | Complete substitution | Other
Mixing / agitation | Pressure | LESS | Pressure¦LESS | Less pressure (vacuum) | Flow¦NO | Incorrect pressure differential (downstream pressure higher than upstream) | EARLY | Relative to clock time
Timing / sequence | Pressure | FLUCTUATING | Pressure¦FLUCTUATING | Pressure fluctuation / surge | Flow¦NO | Isolation in error (wrong valve closed, LOTO on wrong equipment) | LATE | Relative to clock time
Rate of change | Temperature | MORE | Temperature¦MORE | More temperature | Flow¦NO | Power failure; instrument air failure (valves go to fail position) | BEFORE | Relative to sequence
Viscosity / density | Temperature | LESS | Temperature¦LESS | Less temperature | Flow¦NO | Control system / DCS / PLC failure; spurious trip | AFTER | Relative to sequence
Molten metal / slag containment | Level | MORE | Level¦MORE | High level | Flow¦NO | Line frozen or solidified (loss of heat tracing or jacket heating) | FASTER | Rate of step / change
Water contact with molten metal / slag | Level | LESS | Level¦LESS | Low level / no level | Flow¦NO | [C] Polymerisation, crystallisation or hydrate formation in the line | SLOWER | Rate of step / change
Cooling water flow (water-cooled elements) | Level | NO | Level¦NO | Low level / no level | Flow¦NO | [S] Molten metal or slag frozen in launder, runner, tap hole or nozzle (skull formation) | FLUCTUATING | Unstable / surging
Water-cooled element integrity | Composition | AS WELL AS | Composition¦AS WELL AS | Contamination / composition change (As well as) | Flow¦NO | [S] Blocked tuyere, lance tip, burner or porous plug | LOSS OF | Loss of function or containment
Process gas (CO, H2 – BFG, COG, LD gas, reducing gas) | Composition | PART OF | Composition¦PART OF | Part of (wrong ratio / concentration) | Flow¦NO | [S] Bridging / hang-up of burden, DRI, pellets or scrap in bins, chutes or shaft furnace | LEAK OF | Release from containment
Air / oxygen in process gas | Composition | OTHER THAN | Composition¦OTHER THAN | Other than (wrong material) | Flow¦NO | [S] Conveyor, feeder or vibratory feeder stopped (belt tear, drive trip, chute blockage) | INADEQUATE | Auxiliary topic not adequately provided
Oxygen (lances, burners, pipelines) | Phase | OTHER THAN | Phase¦OTHER THAN | Unintended phase change | Flow¦REVERSE | Defective or passing non-return valve | REVIEW | Overview topic (whole-study review)
Inert gas (N2, Ar) | Reaction | MORE | Reaction¦MORE | More reaction / runaway | Flow¦REVERSE | Siphon effect
Electrical energy (furnace / electrolysis) | Reaction | LESS | Reaction¦LESS | Less / no reaction | Flow¦REVERSE | Incorrect differential pressure
Solid charge materials | Reaction | NO | Reaction¦NO | Less / no reaction | Flow¦REVERSE | Two-way flow in common headers
Hot DRI / HBI temperature | Reaction | OTHER THAN | Reaction¦OTHER THAN | Unwanted side reaction (Other than) | Flow¦REVERSE | Poor isolation / passing valves
Combustible dust | Mixing / agitation | NO | Mixing / agitation¦NO | No / less / more mixing | Flow¦REVERSE | Emergency venting or depressurisation
Hydraulic / lube oil | Mixing / agitation | LESS | Mixing / agitation¦LESS | No / less / more mixing | Flow¦REVERSE | Incorrect operation (valve opened out of sequence)
Load control (cranes, ladle / transfer cars) | Mixing / agitation | MORE | Mixing / agitation¦MORE | No / less / more mixing | Flow¦REVERSE | Pump failure or pump running in reverse (wrong rotation after motor rewiring)
Casting speed / mould level | Timing / sequence | EARLY | Timing / sequence¦EARLY | Early / late / before / after / step omitted | Flow¦REVERSE | [C] Process fluid backflow into utility lines (nitrogen, steam, cooling water, potable water) when utility pressure is lower than process
Refractory | Timing / sequence | LATE | Timing / sequence¦LATE | Early / late / before / after / step omitted | Flow¦REVERSE | [S] CO-rich process gas (BFG, COG, BOF/LD gas, DRI top gas) backflowing into nitrogen, air or steam headers
Pickling acid / zinc bath | Timing / sequence | BEFORE | Timing / sequence¦BEFORE | Early / late / before / after / step omitted | Flow¦REVERSE | [S] Flashback in fuel-gas, oxygen or oxy-fuel lines (flame arrestor missing or failed)
Relief | Timing / sequence | AFTER | Timing / sequence¦AFTER | Early / late / before / after / step omitted | Flow¦REVERSE | [S] Loss of water seal / seal pot allowing gas back-flow into the plant or atmosphere
Process control / instrumentation | Timing / sequence | NO | Timing / sequence¦NO | Early / late / before / after / step omitted | Flow¦REVERSE | [S] Reverse flow of cooling water due to loss of pump with elevated header (draining of cooling circuits)
Sampling | Rate of change | FASTER | Rate of change¦FASTER | Faster / slower | Flow¦MORE | High level in upstream vessel (higher static head)
Corrosion / erosion | Rate of change | SLOWER | Rate of change¦SLOWER | Faster / slower | Flow¦MORE | Increased pumping capacity (parallel pumps started, larger impeller fitted)
Utilities / services | Viscosity / density | MORE | Viscosity / density¦MORE | More / less viscosity or density | Flow¦MORE | Increased suction pressure / reduced delivery head
Maintenance | Viscosity / density | LESS | Viscosity / density¦LESS | More / less viscosity or density | Flow¦MORE | Greater fluid density
Spare equipment | Molten metal / slag containment | LOSS OF | Molten metal / slag containment¦LOSS OF | Loss of containment (breakout, spill, splash) | Flow¦MORE | Exchanger tube leaks (high-pressure side into low-pressure side)
Electrical safety / static | Water contact with molten metal / slag | AS WELL AS | Water contact with molten metal / slag¦AS WELL AS | Molten metal / slag contact with water (As well as) | Flow¦MORE | Restriction orifice plates deleted or scale dislodged
Operator action | Cooling water flow (water-cooled elements) | NO | Cooling water flow (water-cooled elements)¦NO | No / less cooling water | Flow¦MORE | Cross-connection of systems
Simplicity | Cooling water flow (water-cooled elements) | LESS | Cooling water flow (water-cooled elements)¦LESS | No / less cooling water | Flow¦MORE | Control faults – control valve fails open, bypass left open, wrong set point
Output – reliability and bottlenecks | Water-cooled element integrity | LOSS OF | Water-cooled element integrity¦LOSS OF | Water leak into furnace / vessel | Flow¦MORE | Two-phase flow
Efficiency – losses | Process gas (CO, H2 – BFG, COG, LD gas, reducing gas) | LEAK OF | Process gas (CO, H2 – BFG, COG, LD gas, reducing gas)¦LEAK OF | Toxic release (Other than / As well as) | Flow¦MORE | Power failure (valves failing open)
Construction | Air / oxygen in process gas | AS WELL AS | Air / oxygen in process gas¦AS WELL AS | Explosive mixture (air or oxygen in gas) | Flow¦MORE | [C] Reagent dosing pump over-delivery (wrong stroke setting)
Commissioning | Oxygen (lances, burners, pipelines) | LEAK OF | Oxygen (lances, burners, pipelines)¦LEAK OF | Oxygen fire / oxygen enrichment | Flow¦MORE | [S] Excessive oxygen flow to lance, burners or tuyeres (flow controller fault, wrong recipe)
Start-up | Oxygen (lances, burners, pipelines) | AS WELL AS | Oxygen (lances, burners, pipelines)¦AS WELL AS | Oxygen fire / oxygen enrichment | Flow¦MORE | [S] Over-feeding of DRI, scrap, fluxes or alloys (feeder speed, weigh-hopper failure)
Shutdown (isolation, purging) | Inert gas (N2, Ar) | LEAK OF | Inert gas (N2, Ar)¦LEAK OF | Asphyxiation / loss of inerting | Flow¦MORE | [S] Excess fuel gas to reheat furnace, ladle pre-heater or stove burners
Breakdown (including service failure) | Inert gas (N2, Ar) | LOSS OF | Inert gas (N2, Ar)¦LOSS OF | Asphyxiation / loss of inerting | Flow¦LESS | Low level in upstream vessel
Materials | Electrical energy (furnace / electrolysis) | MORE | Electrical energy (furnace / electrolysis)¦MORE | More / less / other than intended | Flow¦LESS | Line restriction; valve partly closed
Utilities and services | Electrical energy (furnace / electrolysis) | LESS | Electrical energy (furnace / electrolysis)¦LESS | More / less / other than intended | Flow¦LESS | Filter or strainer blockage
Toxicity | Electrical energy (furnace / electrolysis) | OTHER THAN | Electrical energy (furnace / electrolysis)¦OTHER THAN | More / less / other than intended | Flow¦LESS | Pipe or vessel leakage
Fire and explosion | Solid charge materials | OTHER THAN | Solid charge materials¦OTHER THAN | Wrong / contaminated / excess charge | Flow¦LESS | Defective pumps (worn impeller, cavitation, air ingress, seal failure)
Environmental impact | Solid charge materials | AS WELL AS | Solid charge materials¦AS WELL AS | Wrong / contaminated / excess charge | Flow¦LESS | Fouling of vessels, valves, restrictors or orifice plates
Natural hazards | Solid charge materials | MORE | Solid charge materials¦MORE | Wrong / contaminated / excess charge | Flow¦LESS | Density or viscosity problems
Quality and consistency | Hot DRI / HBI temperature | MORE | Hot DRI / HBI temperature¦MORE | Self-heating / fire / gas generation | Flow¦LESS | Incorrect specification of process fluid
Procedures – development and documentation | Combustible dust | MORE | Combustible dust¦MORE | Dust cloud / ignition | Flow¦LESS | Two-phase flow
Safety equipment | Hydraulic / lube oil | LEAK OF | Hydraulic / lube oil¦LEAK OF | Leak / fire / loss of pressure | Flow¦LESS | [C] Catalyst bed plugging or high pressure drop
Egress / access | Hydraulic / lube oil | LESS | Hydraulic / lube oil¦LESS | Leak / fire / loss of pressure | Flow¦LESS | [S] Scale, silt or biological fouling in cooling passages of panels, roof, tuyeres, staves, lances or copper moulds
Entry / exit points | Load control (cranes, ladle / transfer cars) | LOSS OF | Load control (cranes, ladle / transfer cars)¦LOSS OF | Failure / collision / dropped load | Flow¦LESS | [S] Partly blocked tap hole or nozzle (low tapping rate)
Layout and facility siting | Casting speed / mould level | MORE | Casting speed / mould level¦MORE | Casting speed / mould level / product handling deviations | Flow¦LESS | [S] Dust build-up in off-gas ducts, fans, baghouses or venturi scrubbers
| Casting speed / mould level | LESS | Casting speed / mould level¦LESS | Casting speed / mould level / product handling deviations | Flow¦OTHER THAN | Cross-connection between systems; wrong hose connected
| Refractory | LESS | Refractory¦LESS | Less / failed refractory | Flow¦OTHER THAN | Road / rail tanker discharged into wrong storage tank
| Pickling acid / zinc bath | MORE | Pickling acid / zinc bath¦MORE | Concentration / temperature / contamination deviations | Flow¦OTHER THAN | Drain or vent valves left open
| Pickling acid / zinc bath | LESS | Pickling acid / zinc bath¦LESS | Concentration / temperature / contamination deviations | Flow¦OTHER THAN | Utility station connected to process (nitrogen hose left connected)
| Pickling acid / zinc bath | AS WELL AS | Pickling acid / zinc bath¦AS WELL AS | Concentration / temperature / contamination deviations | Flow¦OTHER THAN | [S] Molten metal or slag spilled outside ladle, pot or mould (ladle misaligned, crane positioning error, tilting over-travel)
| Relief | INADEQUATE | Relief¦INADEQUATE | Inadequate / inappropriate relief | Flow¦OTHER THAN | [S] Slag carry-over into ladle or tundish
| Process control / instrumentation | LOSS OF | Process control / instrumentation¦LOSS OF | Control or safety instrumented function failure | Flow¦OTHER THAN | [S] Off-gas diverted to the wrong system (flare / stack / gas holder change-over error)
| Sampling | INADEQUATE | Sampling¦INADEQUATE | Sampling error / exposure | Flow¦AS WELL AS | Gas or air entrainment in liquid; liquid carry-over in gas
| Corrosion / erosion | MORE | Corrosion / erosion¦MORE | More corrosion / erosion | Flow¦AS WELL AS | Water in hydrocarbon or solvent
| Utilities / services | LOSS OF | Utilities / services¦LOSS OF | Loss of utility / service | Flow¦AS WELL AS | [C] Unreacted material carried forward to next stage
| Maintenance | INADEQUATE | Maintenance¦INADEQUATE | Unsafe maintenance conditions | Flow¦AS WELL AS | [S] Water, ice or snow carried into the furnace with wet scrap, DRI or fluxes
| Spare equipment | NO | Spare equipment¦NO | Unavailability / wrong spares | Flow¦AS WELL AS | [S] Entrained dust or fines in process gas (cyclone or scrubber failure)
| Electrical safety / static | INADEQUATE | Electrical safety / static¦INADEQUATE | Ignition source / electrical hazard | Flow¦AS WELL AS | [S] Oil, grease or paint on scrap generating fume and fire
| Operator action | OTHER THAN | Operator action¦OTHER THAN | Operator error / omission | Pressure¦MORE | Surge problems (water hammer, fast-closing valves)
| Operator action | NO | Operator action¦NO | Operator error / omission | Pressure¦MORE | Leakage from interconnected high-pressure system
| Simplicity | REVIEW | Simplicity¦REVIEW | Unnecessary complexity | Pressure¦MORE | Gas breakthrough (inadequate venting / pressure relief)
| Output – reliability and bottlenecks | REVIEW | Output – reliability and bottlenecks¦REVIEW | Less output / unreliability | Pressure¦MORE | Isolation procedures for relief valves defective (relief valve isolated)
| Efficiency – losses | REVIEW | Efficiency – losses¦REVIEW | Loss of material, energy or conversion | Pressure¦MORE | Thermal overpressure / flashing / boiling / external fire
| Construction | REVIEW | Construction¦REVIEW | Construction hazards and impacts | Pressure¦MORE | Decomposition / gas evolution
| Commissioning | REVIEW | Commissioning¦REVIEW | Commissioning not controlled | Pressure¦MORE | Runaway reaction
| Start-up | REVIEW | Start-up¦REVIEW | Unsafe start-up | Pressure¦MORE | Positive displacement pumps or compressors against closed outlet
| Shutdown (isolation, purging) | REVIEW | Shutdown (isolation, purging)¦REVIEW | Unsafe shutdown | Pressure¦MORE | Failed-open pressure control valves (PCVs)
| Breakdown (including service failure) | REVIEW | Breakdown (including service failure)¦REVIEW | Breakdown / loss of services | Pressure¦MORE | Incorrect operation
| Materials | REVIEW | Materials¦REVIEW | Wrong / inadequate materials of construction | Pressure¦MORE | Blocked outlet, blocked vent or blocked flare / stack
| Utilities and services | REVIEW | Utilities and services¦REVIEW | Inadequate utilities | Pressure¦MORE | Thermal expansion of trapped (blocked-in) liquid
| Toxicity | REVIEW | Toxicity¦REVIEW | Toxic exposure | Pressure¦MORE | [S] Steam generation from water contacting molten metal or slag (water-cooled element leak, wet charge)
| Fire and explosion | REVIEW | Fire and explosion¦REVIEW | Fire / explosion | Pressure¦MORE | [S] Furnace or converter off-gas pressure excursion (loss of draft fan, damper closed, slopping)
| Environmental impact | REVIEW | Environmental impact¦REVIEW | Release to environment | Pressure¦MORE | [S] Blast-furnace top-pressure surge from burden slip / hanging; hot-blast stove valve fault
| Natural hazards | REVIEW | Natural hazards¦REVIEW | External natural event | Pressure¦MORE | [S] Gas holder over-fill or seal failure (BFG, COG, LD gas)
| Quality and consistency | REVIEW | Quality and consistency¦REVIEW | Off-spec product / variability | Pressure¦MORE | [S] Hydraulic system overpressure (relief valve set wrongly, accumulator)
| Procedures – development and documentation | REVIEW | Procedures – development and documentation¦REVIEW | Missing / inadequate procedures | Pressure¦LESS | Generation of vacuum condition (pumping out with vent closed, steam-out then cooling)
| Safety equipment | REVIEW | Safety equipment¦REVIEW | Missing / inadequate safety equipment | Pressure¦LESS | Condensation
| Egress / access | REVIEW | Egress / access¦REVIEW | Inadequate egress or access | Pressure¦LESS | Gas dissolving in liquid
| Entry / exit points | REVIEW | Entry / exit points¦REVIEW | Unsafe entry / exit arrangement | Pressure¦LESS | Restricted pump / compressor suction line
| Layout and facility siting | REVIEW | Layout and facility siting¦REVIEW | Domino / escalation effects | Pressure¦LESS | Undetected leakage
[5 empty] | Pressure¦LESS | Vessel drainage
[5 empty] | Pressure¦LESS | Power failure
[5 empty] | Pressure¦LESS | Incorrect operation
[5 empty] | Pressure¦LESS | Vacuum breaker or vent blocked or frozen
[5 empty] | Pressure¦LESS | [S] Loss of furnace pressure control – air drawn into CO-rich or H2-rich system forming a flammable mixture
[5 empty] | Pressure¦LESS | [S] Vacuum degassing (RH / VD / VOD) – vacuum pump or steam ejector failure, vessel seal leak
[5 empty] | Pressure¦LESS | [S] Low fuel-gas pressure at burners (flame-out followed by re-ignition of accumulated gas)
[5 empty] | Pressure¦LESS | [S] Low cooling-water pressure to water-cooled elements (pump trip, header leak)
[5 empty] | Pressure¦FLUCTUATING | Water hammer; rapid valve closure; pump start/stop
[5 empty] | Pressure¦FLUCTUATING | Compressor or fan surge
[5 empty] | Pressure¦FLUCTUATING | Slug flow / two-phase flow
[5 empty] | Pressure¦FLUCTUATING | Control loop instability
[5 empty] | Pressure¦FLUCTUATING | [S] Converter slopping or foaming slag eruption
[5 empty] | Pressure¦FLUCTUATING | [S] Explosive spalling of wet refractory
[5 empty] | Temperature¦MORE | Ambient conditions (hot weather, solar gain)
[5 empty] | Temperature¦MORE | Fouled or failed exchanger tubes
[5 empty] | Temperature¦MORE | Fire situation
[5 empty] | Temperature¦MORE | Cooling water failure
[5 empty] | Temperature¦MORE | Defective control (TIC fault, heater fails on)
[5 empty] | Temperature¦MORE | Reaction control failures
[5 empty] | Temperature¦MORE | Power failure (loss of cooling fans or pumps)
[5 empty] | Temperature¦MORE | Heat tracing or jacket heating fails on
[5 empty] | Temperature¦MORE | [C] Exothermic reaction / catalyst hot-spot; loss of quench
[5 empty] | Temperature¦MORE | [S] Loss of cooling water to panels, roof, tuyeres, staves, lances or moulds – burn-through
[5 empty] | Temperature¦MORE | [S] Refractory wear or loss – shell hot-spot, breakout
[5 empty] | Temperature¦MORE | [S] Excessive metal superheat (power-on time too long, temperature measurement error)
[5 empty] | Temperature¦MORE | [S] Hot DRI / HBI self-heating and re-oxidation in bins, silos or conveyors
[5 empty] | Temperature¦MORE | [S] Reheat furnace over-firing; burner management failure
[5 empty] | Temperature¦MORE | [S] Hot material on conveyors not rated for the temperature (belt fire)
[5 empty] | Temperature¦LESS | Ambient conditions (cold weather, freezing)
[5 empty] | Temperature¦LESS | Reducing pressure (auto-refrigeration of LPG, CO2, ammonia)
[5 empty] | Temperature¦LESS | Fouled or failed exchanger tubes
[5 empty] | Temperature¦LESS | Loss of heating (steam, hot oil, electric tracing)
[5 empty] | Temperature¦LESS | Power failure
[5 empty] | Temperature¦LESS | Brittle fracture of carbon steel below its minimum design metal temperature
[5 empty] | Temperature¦LESS | [C] Crystallisation, hydrate formation or high viscosity
[5 empty] | Temperature¦LESS | [S] Metal freeze in ladle, tundish, launder or nozzle (low tap temperature, delays)
[5 empty] | Temperature¦LESS | [S] Insufficient pre-heat of ladles, tundishes, moulds or tools – moisture and thermal shock
[5 empty] | Temperature¦LESS | [S] Low reducing-gas temperature – incomplete reduction / carbon deposition
[5 empty] | Level¦MORE | Inlet flow greater than outlet; outlet blocked or valve closed
[5 empty] | Level¦MORE | Level controller or level transmitter failure
[5 empty] | Level¦MORE | Wrong vessel being filled
[5 empty] | Level¦MORE | Overfill during transfer or tanker offloading
[5 empty] | Level¦MORE | [C] Foaming
[5 empty] | Level¦MORE | [S] Over-filling of ladle at tap (molten metal / slag spill)
[5 empty] | Level¦MORE | [S] High mould level in continuous caster (overflow)
[5 empty] | Level¦MORE | [S] Foaming slag over the sill / door
[5 empty] | Level¦MORE | [S] Bin, silo or hopper over-fill (DRI, pellets, coal, lime) – spillage, structural overload
[5 empty] | Level¦LESS | Loss of feed; drain left open; leak
[5 empty] | Level¦LESS | Level indication fails high (false reading)
[5 empty] | Level¦LESS | Pump cavitation or loss of suction
[5 empty] | Level¦LESS | Gas blow-by to downstream low-pressure vessel
[5 empty] | Level¦LESS | [S] Low tundish level – slag entrainment, vortexing
[5 empty] | Level¦LESS | [S] Low water level in seal pots or water seals – gas escape
[5 empty] | Level¦LESS | [S] Low level in boiler drum or evaporative cooling system – overheating
[5 empty] | Level¦LESS | [S] Empty bin or hopper allowing gas to pass back through feed system (loss of material seal)
[5 empty] | Level¦NO | Loss of feed; drain left open; leak
[5 empty] | Level¦NO | Level indication fails high (false reading)
[5 empty] | Level¦NO | Pump cavitation or loss of suction
[5 empty] | Level¦NO | Gas blow-by to downstream low-pressure vessel
[5 empty] | Level¦NO | [S] Low tundish level – slag entrainment, vortexing
[5 empty] | Level¦NO | [S] Low water level in seal pots or water seals – gas escape
[5 empty] | Level¦NO | [S] Low level in boiler drum or evaporative cooling system – overheating
[5 empty] | Level¦NO | [S] Empty bin or hopper allowing gas to pass back through feed system (loss of material seal)
[5 empty] | Composition¦AS WELL AS | Leaking exchanger tubes or isolation valves
[5 empty] | Composition¦AS WELL AS | Incorrect operation of system
[5 empty] | Composition¦AS WELL AS | Interconnected systems
[5 empty] | Composition¦AS WELL AS | Effect of corrosion
[5 empty] | Composition¦AS WELL AS | Wrong additives
[5 empty] | Composition¦AS WELL AS | Ingress of air, water or lubricant
[5 empty] | Composition¦AS WELL AS | Shutdown and start-up conditions
[5 empty] | Composition¦AS WELL AS | Phase change
[5 empty] | Composition¦AS WELL AS | Sediments / scale
[5 empty] | Composition¦AS WELL AS | Biological activity
[5 empty] | Composition¦AS WELL AS | Reaction by-products / breakdown products
[5 empty] | Composition¦AS WELL AS | [C] Catalyst poisons in feed
[5 empty] | Composition¦AS WELL AS | [S] Wet or contaminated scrap – sealed containers, explosives, oil, paint, plastics, radioactive sources
[5 empty] | Composition¦AS WELL AS | [S] Moisture in ferro-alloys, fluxes, ladle additions or tundish powders
[5 empty] | Composition¦AS WELL AS | [S] Oxygen or air ingress into reducing gas or inerted systems
[5 empty] | Composition¦AS WELL AS | [S] Hydrogen, CO or H2S in process gas above design values
[5 empty] | Composition¦PART OF | Feed ratio controller failure; one feed lost
[5 empty] | Composition¦PART OF | Dosing pump stopped or air-locked
[5 empty] | Composition¦PART OF | Analyser or sample error
[5 empty] | Composition¦PART OF | [C] Wrong acid or caustic concentration
[5 empty] | Composition¦PART OF | [S] Carbon, sulphur or metallisation of DRI outside specification
[5 empty] | Composition¦PART OF | [S] Wrong fuel / air ratio – incomplete combustion, CO formation
[5 empty] | Composition¦PART OF | [S] Pickling acid strength out of range
[5 empty] | Composition¦OTHER THAN | Wrong raw material delivered or unloaded
[5 empty] | Composition¦OTHER THAN | Mislabelled drums, IBCs or cylinders
[5 empty] | Composition¦OTHER THAN | Wrong gas connected (e.g. oxygen in place of nitrogen, nitrogen in place of breathing air)
[5 empty] | Composition¦OTHER THAN | Incorrect hose / coupling standardisation
[5 empty] | Composition¦OTHER THAN | [S] Wrong alloy addition or wrong grade of scrap charged
[5 empty] | Phase¦OTHER THAN | Flashing, boiling or condensation
[5 empty] | Phase¦OTHER THAN | Freezing or solidification
[5 empty] | Phase¦OTHER THAN | Two-phase flow in single-phase design
[5 empty] | Phase¦OTHER THAN | [C] Vapour lock; liquid in compressor suction
[5 empty] | Phase¦OTHER THAN | [S] Molten metal–water contact – steam explosion
[5 empty] | Phase¦OTHER THAN | [S] Solidification of slag or metal in transfer equipment
[5 empty] | Reaction¦MORE | Loss of cooling or agitation
[5 empty] | Reaction¦MORE | Excess catalyst or initiator; wrong reactant order
[5 empty] | Reaction¦MORE | Higher feed concentration or temperature
[5 empty] | Reaction¦MORE | Accumulation of unreacted material followed by sudden reaction
[5 empty] | Reaction¦MORE | [C] Contamination promoting decomposition
[5 empty] | Reaction¦MORE | [S] Excessive oxygen blowing – violent carbon boil / slopping
[5 empty] | Reaction¦MORE | [S] Metal–water reaction generating hydrogen
[5 empty] | Reaction¦MORE | [S] Aluminium, magnesium or other reactive metal powders in contact with water
[5 empty] | Reaction¦LESS | Low temperature; catalyst deactivated
[5 empty] | Reaction¦LESS | Wrong or missing reactant; inhibitor excess
[5 empty] | Reaction¦LESS | [C] Accumulation of unreacted material (later runaway)
[5 empty] | Reaction¦LESS | [S] Incomplete reduction in DRI shaft / kiln (low metallisation)
[5 empty] | Reaction¦LESS | [S] Low reducing-gas quality or temperature
[5 empty] | Reaction¦NO | Low temperature; catalyst deactivated
[5 empty] | Reaction¦NO | Wrong or missing reactant; inhibitor excess
[5 empty] | Reaction¦NO | [C] Accumulation of unreacted material (later runaway)
[5 empty] | Reaction¦NO | [S] Incomplete reduction in DRI shaft / kiln (low metallisation)
[5 empty] | Reaction¦NO | [S] Low reducing-gas quality or temperature
[5 empty] | Reaction¦OTHER THAN | [C] Decomposition, polymerisation, oxidation
[5 empty] | Reaction¦OTHER THAN | [S] Carbon deposition (Boudouard reaction) in reducing-gas systems
[5 empty] | Reaction¦OTHER THAN | [S] Carbonyl formation where CO contacts nickel or iron surfaces at low temperature
[5 empty] | Reaction¦OTHER THAN | [S] Re-oxidation of DRI / HBI (heat and hydrogen release)
[5 empty] | Reaction¦OTHER THAN | Toxic gas evolution (H2S, HCN, NOx, phosphine from wetted ferro-silicon)
[5 empty] | Mixing / agitation¦NO | Agitator, mixer or circulation pump trip
[5 empty] | Mixing / agitation¦NO | Wrong agitator speed
[5 empty] | Mixing / agitation¦NO | [C] Stratification of reactants
[5 empty] | Mixing / agitation¦NO | [S] Argon / nitrogen stirring – porous plug blocked or leaking
[5 empty] | Mixing / agitation¦NO | [S] Excessive stirring – metal splash, slag entrainment
[5 empty] | Mixing / agitation¦NO | [S] Electromagnetic stirrer failure
[5 empty] | Mixing / agitation¦LESS | Agitator, mixer or circulation pump trip
[5 empty] | Mixing / agitation¦LESS | Wrong agitator speed
[5 empty] | Mixing / agitation¦LESS | [C] Stratification of reactants
[5 empty] | Mixing / agitation¦LESS | [S] Argon / nitrogen stirring – porous plug blocked or leaking
[5 empty] | Mixing / agitation¦LESS | [S] Excessive stirring – metal splash, slag entrainment
[5 empty] | Mixing / agitation¦LESS | [S] Electromagnetic stirrer failure
[5 empty] | Mixing / agitation¦MORE | Agitator, mixer or circulation pump trip
[5 empty] | Mixing / agitation¦MORE | Wrong agitator speed
[5 empty] | Mixing / agitation¦MORE | [C] Stratification of reactants
[5 empty] | Mixing / agitation¦MORE | [S] Argon / nitrogen stirring – porous plug blocked or leaking
[5 empty] | Mixing / agitation¦MORE | [S] Excessive stirring – metal splash, slag entrainment
[5 empty] | Mixing / agitation¦MORE | [S] Electromagnetic stirrer failure
[5 empty] | Timing / sequence¦EARLY | Procedure step skipped or done out of order
[5 empty] | Timing / sequence¦EARLY | Batch timer or sequence controller failure
[5 empty] | Timing / sequence¦EARLY | Purge time too short before light-up (burner management)
[5 empty] | Timing / sequence¦EARLY | Operator distraction or shift changeover
[5 empty] | Timing / sequence¦EARLY | [C] Reagent added before reaction mass at temperature
[5 empty] | Timing / sequence¦EARLY | [S] Tapping late (over-oxidation, high temperature) or early (low temperature)
[5 empty] | Timing / sequence¦EARLY | [S] Oxygen on before lance in correct position; lance not withdrawn at end of blow
[5 empty] | Timing / sequence¦EARLY | [S] Charging scrap into a furnace with water present or hot heel too large
[5 empty] | Timing / sequence¦EARLY | [S] Ladle not dried out / pre-heated before use
[5 empty] | Timing / sequence¦LATE | Procedure step skipped or done out of order
[5 empty] | Timing / sequence¦LATE | Batch timer or sequence controller failure
[5 empty] | Timing / sequence¦LATE | Purge time too short before light-up (burner management)
[5 empty] | Timing / sequence¦LATE | Operator distraction or shift changeover
[5 empty] | Timing / sequence¦LATE | [C] Reagent added before reaction mass at temperature
[5 empty] | Timing / sequence¦LATE | [S] Tapping late (over-oxidation, high temperature) or early (low temperature)
[5 empty] | Timing / sequence¦LATE | [S] Oxygen on before lance in correct position; lance not withdrawn at end of blow
[5 empty] | Timing / sequence¦LATE | [S] Charging scrap into a furnace with water present or hot heel too large
[5 empty] | Timing / sequence¦LATE | [S] Ladle not dried out / pre-heated before use
[5 empty] | Timing / sequence¦BEFORE | Procedure step skipped or done out of order
[5 empty] | Timing / sequence¦BEFORE | Batch timer or sequence controller failure
[5 empty] | Timing / sequence¦BEFORE | Purge time too short before light-up (burner management)
[5 empty] | Timing / sequence¦BEFORE | Operator distraction or shift changeover
[5 empty] | Timing / sequence¦BEFORE | [C] Reagent added before reaction mass at temperature
[5 empty] | Timing / sequence¦BEFORE | [S] Tapping late (over-oxidation, high temperature) or early (low temperature)
[5 empty] | Timing / sequence¦BEFORE | [S] Oxygen on before lance in correct position; lance not withdrawn at end of blow
[5 empty] | Timing / sequence¦BEFORE | [S] Charging scrap into a furnace with water present or hot heel too large
[5 empty] | Timing / sequence¦BEFORE | [S] Ladle not dried out / pre-heated before use
[5 empty] | Timing / sequence¦AFTER | Procedure step skipped or done out of order
[5 empty] | Timing / sequence¦AFTER | Batch timer or sequence controller failure
[5 empty] | Timing / sequence¦AFTER | Purge time too short before light-up (burner management)
[5 empty] | Timing / sequence¦AFTER | Operator distraction or shift changeover
[5 empty] | Timing / sequence¦AFTER | [C] Reagent added before reaction mass at temperature
[5 empty] | Timing / sequence¦AFTER | [S] Tapping late (over-oxidation, high temperature) or early (low temperature)
[5 empty] | Timing / sequence¦AFTER | [S] Oxygen on before lance in correct position; lance not withdrawn at end of blow
[5 empty] | Timing / sequence¦AFTER | [S] Charging scrap into a furnace with water present or hot heel too large
[5 empty] | Timing / sequence¦AFTER | [S] Ladle not dried out / pre-heated before use
[5 empty] | Timing / sequence¦NO | Procedure step skipped or done out of order
[5 empty] | Timing / sequence¦NO | Batch timer or sequence controller failure
[5 empty] | Timing / sequence¦NO | Purge time too short before light-up (burner management)
[5 empty] | Timing / sequence¦NO | Operator distraction or shift changeover
[5 empty] | Timing / sequence¦NO | [C] Reagent added before reaction mass at temperature
[5 empty] | Timing / sequence¦NO | [S] Tapping late (over-oxidation, high temperature) or early (low temperature)
[5 empty] | Timing / sequence¦NO | [S] Oxygen on before lance in correct position; lance not withdrawn at end of blow
[5 empty] | Timing / sequence¦NO | [S] Charging scrap into a furnace with water present or hot heel too large
[5 empty] | Timing / sequence¦NO | [S] Ladle not dried out / pre-heated before use
[5 empty] | Rate of change¦FASTER | Ramp rate too fast for equipment or refractory
[5 empty] | Rate of change¦FASTER | [S] Casting speed too fast – breakout
[5 empty] | Rate of change¦FASTER | [S] Heat-up / dry-out of new refractory too fast – spalling
[5 empty] | Rate of change¦FASTER | [S] Crane travel or tilting too fast – metal splash
[5 empty] | Rate of change¦SLOWER | Ramp rate too fast for equipment or refractory
[5 empty] | Rate of change¦SLOWER | [S] Casting speed too fast – breakout
[5 empty] | Rate of change¦SLOWER | [S] Heat-up / dry-out of new refractory too fast – spalling
[5 empty] | Rate of change¦SLOWER | [S] Crane travel or tilting too fast – metal splash
[5 empty] | Viscosity / density¦MORE | Temperature change
[5 empty] | Viscosity / density¦MORE | Wrong material or concentration
[5 empty] | Viscosity / density¦MORE | Solids content too high
[5 empty] | Viscosity / density¦MORE | [S] Slag basicity or chemistry wrong – viscous slag, poor fluidity
[5 empty] | Viscosity / density¦LESS | Temperature change
[5 empty] | Viscosity / density¦LESS | Wrong material or concentration
[5 empty] | Viscosity / density¦LESS | Solids content too high
[5 empty] | Viscosity / density¦LESS | [S] Slag basicity or chemistry wrong – viscous slag, poor fluidity
[5 empty] | Molten metal / slag containment¦LOSS OF | Refractory wear, erosion or spalling; missed refractory inspection
[5 empty] | Molten metal / slag containment¦LOSS OF | Furnace shell or ladle shell burn-through
[5 empty] | Molten metal / slag containment¦LOSS OF | Tap-hole or slide-gate failure; nozzle failure
[5 empty] | Molten metal / slag containment¦LOSS OF | Ladle over-filling
[5 empty] | Molten metal / slag containment¦LOSS OF | Crane failure or dropped ladle; ladle trunnion failure
[5 empty] | Molten metal / slag containment¦LOSS OF | Ladle or pot not correctly seated on car or stand
[5 empty] | Molten metal / slag containment¦LOSS OF | Tilting drive over-travel; loss of hydraulic or electrical control
[5 empty] | Molten metal / slag containment¦LOSS OF | Breakout at caster (mould level, casting speed, lubrication, sticker)
[5 empty] | Molten metal / slag containment¦LOSS OF | Vehicle or ladle-car collision; derailment
[5 empty] | Water contact with molten metal / slag¦AS WELL AS | Leaking water-cooled panel, roof, tuyere, stave, lance or copper mould
[5 empty] | Water contact with molten metal / slag¦AS WELL AS | Wet scrap, DRI, fluxes or ladle additions; snow or ice
[5 empty] | Water contact with molten metal / slag¦AS WELL AS | Wet or damp ladles, tundishes, moulds, tools or slag pots
[5 empty] | Water contact with molten metal / slag¦AS WELL AS | Water on floor or in pits under tapping areas
[5 empty] | Water contact with molten metal / slag¦AS WELL AS | Rain ingress through damaged roofs; flooding
[5 empty] | Water contact with molten metal / slag¦AS WELL AS | Spray cooling water impinging on spilled metal
[5 empty] | Water contact with molten metal / slag¦AS WELL AS | Granulation / slag-pit water management failure
[5 empty] | Cooling water flow (water-cooled elements)¦NO | Pump trip or power failure without emergency (gravity / diesel) supply
[5 empty] | Cooling water flow (water-cooled elements)¦NO | Valve closed in error; header isolation
[5 empty] | Cooling water flow (water-cooled elements)¦NO | Scale, silt or biological fouling
[5 empty] | Cooling water flow (water-cooled elements)¦NO | Air locking of circuits
[5 empty] | Cooling water flow (water-cooled elements)¦NO | Low header pressure or tank level
[5 empty] | Cooling water flow (water-cooled elements)¦NO | Cooling tower failure (fans, basin level)
[5 empty] | Cooling water flow (water-cooled elements)¦LESS | Pump trip or power failure without emergency (gravity / diesel) supply
[5 empty] | Cooling water flow (water-cooled elements)¦LESS | Valve closed in error; header isolation
[5 empty] | Cooling water flow (water-cooled elements)¦LESS | Scale, silt or biological fouling
[5 empty] | Cooling water flow (water-cooled elements)¦LESS | Air locking of circuits
[5 empty] | Cooling water flow (water-cooled elements)¦LESS | Low header pressure or tank level
[5 empty] | Cooling water flow (water-cooled elements)¦LESS | Cooling tower failure (fans, basin level)
[5 empty] | Water-cooled element integrity¦LOSS OF | Thermal fatigue cracking of panels or lance
[5 empty] | Water-cooled element integrity¦LOSS OF | Arc or flame impingement damage
[5 empty] | Water-cooled element integrity¦LOSS OF | Mechanical damage from scrap charging
[5 empty] | Water-cooled element integrity¦LOSS OF | Erosion or corrosion (water chemistry)
[5 empty] | Water-cooled element integrity¦LOSS OF | Poor weld or repair quality
[5 empty] | Water-cooled element integrity¦LOSS OF | Over-pressure of closed circuit
[5 empty] | Water-cooled element integrity¦LOSS OF | Leak detection (flow in/out differential) failed or not fitted
[5 empty] | Process gas (CO, H2 – BFG, COG, LD gas, reducing gas)¦LEAK OF | Flange, valve or seal leak; water-seal blown
[5 empty] | Process gas (CO, H2 – BFG, COG, LD gas, reducing gas)¦LEAK OF | Gas back-flow into buildings via drains or cable ducts
[5 empty] | Process gas (CO, H2 – BFG, COG, LD gas, reducing gas)¦LEAK OF | Bleeder / relief opening near work areas
[5 empty] | Process gas (CO, H2 – BFG, COG, LD gas, reducing gas)¦LEAK OF | Isolation failure during maintenance (no double block and bleed, no blinding)
[5 empty] | Process gas (CO, H2 – BFG, COG, LD gas, reducing gas)¦LEAK OF | Gas detection inoperative or poorly located
[5 empty] | Process gas (CO, H2 – BFG, COG, LD gas, reducing gas)¦LEAK OF | Confined spaces near gas mains
[5 empty] | Air / oxygen in process gas¦AS WELL AS | Air ingress through leaks at negative pressure
[5 empty] | Air / oxygen in process gas¦AS WELL AS | Inadequate purging at start-up / shutdown
[5 empty] | Air / oxygen in process gas¦AS WELL AS | Gas holder or collector low pressure
[5 empty] | Air / oxygen in process gas¦AS WELL AS | Oxygen analyser failure on LD gas recovery
[5 empty] | Air / oxygen in process gas¦AS WELL AS | Burner flame-out with continued fuel supply
[5 empty] | Oxygen (lances, burners, pipelines)¦LEAK OF | Oil, grease or debris contamination in oxygen service
[5 empty] | Oxygen (lances, burners, pipelines)¦LEAK OF | High gas velocity / particle impingement in valves and bends
[5 empty] | Oxygen (lances, burners, pipelines)¦LEAK OF | Incompatible materials of construction or gaskets
[5 empty] | Oxygen (lances, burners, pipelines)¦LEAK OF | Fast-opening valves (adiabatic compression)
[5 empty] | Oxygen (lances, burners, pipelines)¦LEAK OF | Leak into enclosed areas – enriched atmosphere, clothing fire
[5 empty] | Oxygen (lances, burners, pipelines)¦LEAK OF | Lance blocked or burned back
[5 empty] | Oxygen (lances, burners, pipelines)¦AS WELL AS | Oil, grease or debris contamination in oxygen service
[5 empty] | Oxygen (lances, burners, pipelines)¦AS WELL AS | High gas velocity / particle impingement in valves and bends
[5 empty] | Oxygen (lances, burners, pipelines)¦AS WELL AS | Incompatible materials of construction or gaskets
[5 empty] | Oxygen (lances, burners, pipelines)¦AS WELL AS | Fast-opening valves (adiabatic compression)
[5 empty] | Oxygen (lances, burners, pipelines)¦AS WELL AS | Leak into enclosed areas – enriched atmosphere, clothing fire
[5 empty] | Oxygen (lances, burners, pipelines)¦AS WELL AS | Lance blocked or burned back
[5 empty] | Inert gas (N2, Ar)¦LEAK OF | Leak or purge into enclosed or confined area
[5 empty] | Inert gas (N2, Ar)¦LEAK OF | Inert gas used as breathing air (wrong connection)
[5 empty] | Inert gas (N2, Ar)¦LEAK OF | Pit, tunnel or bin atmosphere not tested before entry
[5 empty] | Inert gas (N2, Ar)¦LEAK OF | Loss of inert blanketing on DRI bins, coal mills or dust filters
[5 empty] | Inert gas (N2, Ar)¦LEAK OF | Nitrogen supply failure (plant trip)
[5 empty] | Inert gas (N2, Ar)¦LOSS OF | Leak or purge into enclosed or confined area
[5 empty] | Inert gas (N2, Ar)¦LOSS OF | Inert gas used as breathing air (wrong connection)
[5 empty] | Inert gas (N2, Ar)¦LOSS OF | Pit, tunnel or bin atmosphere not tested before entry
[5 empty] | Inert gas (N2, Ar)¦LOSS OF | Loss of inert blanketing on DRI bins, coal mills or dust filters
[5 empty] | Inert gas (N2, Ar)¦LOSS OF | Nitrogen supply failure (plant trip)
[5 empty] | Electrical energy (furnace / electrolysis)¦MORE | Electrode breakage or slipping
[5 empty] | Electrical energy (furnace / electrolysis)¦MORE | Transformer or reactor cooling failure; transformer fire
[5 empty] | Electrical energy (furnace / electrolysis)¦MORE | Over-current or short circuit; regulation fault
[5 empty] | Electrical energy (furnace / electrolysis)¦MORE | Arc flash on high-current bus bars
[5 empty] | Electrical energy (furnace / electrolysis)¦MORE | Loss of furnace power at critical stage (metal freeze)
[5 empty] | Electrical energy (furnace / electrolysis)¦MORE | [S] Electrolysis cells / potlines – DC magnetic fields, anode effect, cell tapping errors
[5 empty] | Electrical energy (furnace / electrolysis)¦LESS | Electrode breakage or slipping
[5 empty] | Electrical energy (furnace / electrolysis)¦LESS | Transformer or reactor cooling failure; transformer fire
[5 empty] | Electrical energy (furnace / electrolysis)¦LESS | Over-current or short circuit; regulation fault
[5 empty] | Electrical energy (furnace / electrolysis)¦LESS | Arc flash on high-current bus bars
[5 empty] | Electrical energy (furnace / electrolysis)¦LESS | Loss of furnace power at critical stage (metal freeze)
[5 empty] | Electrical energy (furnace / electrolysis)¦LESS | [S] Electrolysis cells / potlines – DC magnetic fields, anode effect, cell tapping errors
[5 empty] | Electrical energy (furnace / electrolysis)¦OTHER THAN | Electrode breakage or slipping
[5 empty] | Electrical energy (furnace / electrolysis)¦OTHER THAN | Transformer or reactor cooling failure; transformer fire
[5 empty] | Electrical energy (furnace / electrolysis)¦OTHER THAN | Over-current or short circuit; regulation fault
[5 empty] | Electrical energy (furnace / electrolysis)¦OTHER THAN | Arc flash on high-current bus bars
[5 empty] | Electrical energy (furnace / electrolysis)¦OTHER THAN | Loss of furnace power at critical stage (metal freeze)
[5 empty] | Electrical energy (furnace / electrolysis)¦OTHER THAN | [S] Electrolysis cells / potlines – DC magnetic fields, anode effect, cell tapping errors
[5 empty] | Solid charge materials¦OTHER THAN | Sealed containers, gas cylinders, explosives in scrap
[5 empty] | Solid charge materials¦OTHER THAN | Radioactive sources in scrap (portal monitor failure)
[5 empty] | Solid charge materials¦OTHER THAN | Moisture in charge
[5 empty] | Solid charge materials¦OTHER THAN | Oversize pieces – bridging, mechanical damage
[5 empty] | Solid charge materials¦OTHER THAN | Segregation – inconsistent chemistry
[5 empty] | Solid charge materials¦OTHER THAN | Fines – dust generation
[5 empty] | Solid charge materials¦AS WELL AS | Sealed containers, gas cylinders, explosives in scrap
[5 empty] | Solid charge materials¦AS WELL AS | Radioactive sources in scrap (portal monitor failure)
[5 empty] | Solid charge materials¦AS WELL AS | Moisture in charge
[5 empty] | Solid charge materials¦AS WELL AS | Oversize pieces – bridging, mechanical damage
[5 empty] | Solid charge materials¦AS WELL AS | Segregation – inconsistent chemistry
[5 empty] | Solid charge materials¦AS WELL AS | Fines – dust generation
[5 empty] | Solid charge materials¦MORE | Sealed containers, gas cylinders, explosives in scrap
[5 empty] | Solid charge materials¦MORE | Radioactive sources in scrap (portal monitor failure)
[5 empty] | Solid charge materials¦MORE | Moisture in charge
[5 empty] | Solid charge materials¦MORE | Oversize pieces – bridging, mechanical damage
[5 empty] | Solid charge materials¦MORE | Segregation – inconsistent chemistry
[5 empty] | Solid charge materials¦MORE | Fines – dust generation
[5 empty] | Hot DRI / HBI temperature¦MORE | Re-oxidation in air (insufficient inerting or cooling)
[5 empty] | Hot DRI / HBI temperature¦MORE | Water contact – heat and hydrogen generation
[5 empty] | Hot DRI / HBI temperature¦MORE | Dust and fines accumulation
[5 empty] | Hot DRI / HBI temperature¦MORE | Conveyor or transport vessel over-temperature
[5 empty] | Hot DRI / HBI temperature¦MORE | Long storage times; poor bin ventilation
[5 empty] | Combustible dust¦MORE | Dust accumulation on structures; poor housekeeping
[5 empty] | Combustible dust¦MORE | Dust collector or baghouse fire / explosion
[5 empty] | Combustible dust¦MORE | Hot surfaces, sparks, static, hot work
[5 empty] | Combustible dust¦MORE | Loss of inerting in coal mill or PCI system
[5 empty] | Combustible dust¦MORE | Explosion venting / suppression / isolation missing or ineffective
[5 empty] | Hydraulic / lube oil¦LEAK OF | Hose or fitting failure near hot metal or hot product
[5 empty] | Hydraulic / lube oil¦LEAK OF | Use of mineral oil instead of fire-resistant fluid near hot areas
[5 empty] | Hydraulic / lube oil¦LEAK OF | Accumulator failure – uncontrolled movement
[5 empty] | Hydraulic / lube oil¦LEAK OF | Loss of pressure – uncontrolled tilt, roll gap or clamp release
[5 empty] | Hydraulic / lube oil¦LEAK OF | Contaminated oil – valve sticking
[5 empty] | Hydraulic / lube oil¦LESS | Hose or fitting failure near hot metal or hot product
[5 empty] | Hydraulic / lube oil¦LESS | Use of mineral oil instead of fire-resistant fluid near hot areas
[5 empty] | Hydraulic / lube oil¦LESS | Accumulator failure – uncontrolled movement
[5 empty] | Hydraulic / lube oil¦LESS | Loss of pressure – uncontrolled tilt, roll gap or clamp release
[5 empty] | Hydraulic / lube oil¦LESS | Contaminated oil – valve sticking
[5 empty] | Load control (cranes, ladle / transfer cars)¦LOSS OF | Crane brake, rope or hook failure while carrying molten metal
[5 empty] | Load control (cranes, ladle / transfer cars)¦LOSS OF | Power failure with ladle suspended
[5 empty] | Load control (cranes, ladle / transfer cars)¦LOSS OF | Anti-collision or limit switch failure
[5 empty] | Load control (cranes, ladle / transfer cars)¦LOSS OF | Overload; incorrect lifting accessory
[5 empty] | Load control (cranes, ladle / transfer cars)¦LOSS OF | Poor visibility from steam or fume
[5 empty] | Casting speed / mould level¦MORE | Mould level control failure – overflow or breakout
[5 empty] | Casting speed / mould level¦MORE | Secondary cooling water failure
[5 empty] | Casting speed / mould level¦MORE | Cobbles in rolling mill; product jumping guides
[5 empty] | Casting speed / mould level¦MORE | Roll breakage; drive failure
[5 empty] | Casting speed / mould level¦MORE | Scale-breaker high-pressure water hazards
[5 empty] | Casting speed / mould level¦LESS | Mould level control failure – overflow or breakout
[5 empty] | Casting speed / mould level¦LESS | Secondary cooling water failure
[5 empty] | Casting speed / mould level¦LESS | Cobbles in rolling mill; product jumping guides
[5 empty] | Casting speed / mould level¦LESS | Roll breakage; drive failure
[5 empty] | Casting speed / mould level¦LESS | Scale-breaker high-pressure water hazards
[5 empty] | Refractory¦LESS | Wear beyond limit; inspection missed
[5 empty] | Refractory¦LESS | Wrong refractory specification
[5 empty] | Refractory¦LESS | Inadequate dry-out (moisture – spalling, steam)
[5 empty] | Refractory¦LESS | Thermal shock from rapid heating or cooling
[5 empty] | Refractory¦LESS | Chemical attack by slag
[5 empty] | Pickling acid / zinc bath¦MORE | Acid concentration out of range – fume, over-pickling
[5 empty] | Pickling acid / zinc bath¦MORE | Acid regeneration plant upset – HCl release
[5 empty] | Pickling acid / zinc bath¦MORE | Fume extraction failure
[5 empty] | Pickling acid / zinc bath¦MORE | Wet or contaminated steel entering molten zinc bath – eruption
[5 empty] | Pickling acid / zinc bath¦MORE | Flux or zinc ash handling exposures
[5 empty] | Pickling acid / zinc bath¦LESS | Acid concentration out of range – fume, over-pickling
[5 empty] | Pickling acid / zinc bath¦LESS | Acid regeneration plant upset – HCl release
[5 empty] | Pickling acid / zinc bath¦LESS | Fume extraction failure
[5 empty] | Pickling acid / zinc bath¦LESS | Wet or contaminated steel entering molten zinc bath – eruption
[5 empty] | Pickling acid / zinc bath¦LESS | Flux or zinc ash handling exposures
[5 empty] | Pickling acid / zinc bath¦AS WELL AS | Acid concentration out of range – fume, over-pickling
[5 empty] | Pickling acid / zinc bath¦AS WELL AS | Acid regeneration plant upset – HCl release
[5 empty] | Pickling acid / zinc bath¦AS WELL AS | Fume extraction failure
[5 empty] | Pickling acid / zinc bath¦AS WELL AS | Wet or contaminated steel entering molten zinc bath – eruption
[5 empty] | Pickling acid / zinc bath¦AS WELL AS | Flux or zinc ash handling exposures
[5 empty] | Relief¦INADEQUATE | Relief philosophy not defined for all scenarios (fire, blocked outlet, runaway, tube rupture)
[5 empty] | Relief¦INADEQUATE | Type of relief device and its reliability
[5 empty] | Relief¦INADEQUATE | Relief valve discharge location unsafe (to work areas, ignition sources)
[5 empty] | Relief¦INADEQUATE | Pollution implications of discharge
[5 empty] | Relief¦INADEQUATE | Relief isolated or blocked; incorrect set pressure
[5 empty] | Relief¦INADEQUATE | [S] Explosion doors / bleeders on furnaces and gas mains – location and maintenance
[5 empty] | Process control / instrumentation¦LOSS OF | Control philosophy unclear
[5 empty] | Process control / instrumentation¦LOSS OF | Location of instruments unsuitable
[5 empty] | Process control / instrumentation¦LOSS OF | Response time; set points of alarms and trips
[5 empty] | Process control / instrumentation¦LOSS OF | Time available for operator intervention
[5 empty] | Process control / instrumentation¦LOSS OF | Alarm and trip testing not done
[5 empty] | Process control / instrumentation¦LOSS OF | Fire protection of instruments and cables
[5 empty] | Process control / instrumentation¦LOSS OF | Electronic trip / control amplifiers
[5 empty] | Process control / instrumentation¦LOSS OF | Panel arrangement and location
[5 empty] | Process control / instrumentation¦LOSS OF | Auto / manual facility and human error
[5 empty] | Process control / instrumentation¦LOSS OF | Alarm flooding; bypassed trips
[5 empty] | Process control / instrumentation¦LOSS OF | [S] Instruments in high temperature, dust and EMF environments (temperature probes, level radars, leak detection)
[5 empty] | Sampling¦INADEQUATE | Sampling procedure inadequate
[5 empty] | Sampling¦INADEQUATE | Time for analysis result too long
[5 empty] | Sampling¦INADEQUATE | Calibration of automatic samplers / reliability
[5 empty] | Sampling¦INADEQUATE | Accuracy of representative sample
[5 empty] | Sampling¦INADEQUATE | Diagnosis of result
[5 empty] | Sampling¦INADEQUATE | Exposure of sampler to toxic, hot or pressurised material
[5 empty] | Sampling¦INADEQUATE | [S] Molten metal sampling and temperature measurement at the furnace door or ladle
[5 empty] | Corrosion / erosion¦MORE | Cathodic protection arrangements inadequate
[5 empty] | Corrosion / erosion¦MORE | Internal / external corrosion protection
[5 empty] | Corrosion / erosion¦MORE | Engineering specifications
[5 empty] | Corrosion / erosion¦MORE | Zinc embrittlement
[5 empty] | Corrosion / erosion¦MORE | Stress corrosion cracking (chlorides)
[5 empty] | Corrosion / erosion¦MORE | Fluid velocities too high
[5 empty] | Corrosion / erosion¦MORE | Corrosion under insulation
[5 empty] | Corrosion / erosion¦MORE | [S] Abrasive slurries, dust-laden gas, acid dew-point corrosion in off-gas ducts
[5 empty] | Utilities / services¦LOSS OF | Failure of dry instrument air
[5 empty] | Utilities / services¦LOSS OF | Failure of steam / nitrogen / cooling water
[5 empty] | Utilities / services¦LOSS OF | Failure of hydraulic power / electric power
[5 empty] | Utilities / services¦LOSS OF | Telecommunications
[5 empty] | Utilities / services¦LOSS OF | Heating and ventilating systems
[5 empty] | Utilities / services¦LOSS OF | Computers / control system / network
[5 empty] | Utilities / services¦LOSS OF | [S] Loss of oxygen, argon or natural gas supply from air-separation plant or pipeline
[5 empty] | Maintenance¦INADEQUATE | Isolation, drainage, purging
[5 empty] | Maintenance¦INADEQUATE | Cleaning, drying
[5 empty] | Maintenance¦INADEQUATE | Slip plates
[5 empty] | Maintenance¦INADEQUATE | Access
[5 empty] | Maintenance¦INADEQUATE | Rescue plan
[5 empty] | Maintenance¦INADEQUATE | Training
[5 empty] | Maintenance¦INADEQUATE | Pressure testing
[5 empty] | Maintenance¦INADEQUATE | Work permit system
[5 empty] | Maintenance¦INADEQUATE | Condition monitoring
[5 empty] | Maintenance¦INADEQUATE | [S] Hot work near gas mains or dust; work under suspended loads; work inside cooled-down furnaces
[5 empty] | Spare equipment¦NO | Installed / non-installed spare equipment
[5 empty] | Spare equipment¦NO | Availability of spares
[5 empty] | Spare equipment¦NO | Modified specifications
[5 empty] | Spare equipment¦NO | Storage of spares
[5 empty] | Spare equipment¦NO | Catalogue of spares
[5 empty] | Electrical safety / static¦INADEQUATE | Static discharge
[5 empty] | Electrical safety / static¦INADEQUATE | Earthing arrangements
[5 empty] | Electrical safety / static¦INADEQUATE | Insulated vessels / equipment
[5 empty] | Electrical safety / static¦INADEQUATE | Low-conductance fluids
[5 empty] | Electrical safety / static¦INADEQUATE | Splash filling of vessels
[5 empty] | Electrical safety / static¦INADEQUATE | Insulated strainers and valve components
[5 empty] | Electrical safety / static¦INADEQUATE | Dust generation and handling
[5 empty] | Electrical safety / static¦INADEQUATE | Hoses
[5 empty] | Electrical safety / static¦INADEQUATE | Area classification
[5 empty] | Electrical safety / static¦INADEQUATE | [S] High-current bus bars, induced currents and magnetic fields
[5 empty] | Operator action¦OTHER THAN | Unclear or absent procedures
[5 empty] | Operator action¦OTHER THAN | Poor labelling and identification
[5 empty] | Operator action¦OTHER THAN | Workload, fatigue, shift handover
[5 empty] | Operator action¦OTHER THAN | Alarm overload; poor HMI design
[5 empty] | Operator action¦OTHER THAN | Inadequate training or competence
[5 empty] | Operator action¦NO | Unclear or absent procedures
[5 empty] | Operator action¦NO | Poor labelling and identification
[5 empty] | Operator action¦NO | Workload, fatigue, shift handover
[5 empty] | Operator action¦NO | Alarm overload; poor HMI design
[5 empty] | Operator action¦NO | Inadequate training or competence
[5 empty] | Simplicity¦REVIEW | Can we omit plant or simplify control?
[5 empty] | Simplicity¦REVIEW | Too many interlocks or bypasses
[5 empty] | Output – reliability and bottlenecks¦REVIEW | Least reliable components
[5 empty] | Output – reliability and bottlenecks¦REVIEW | Most limiting components
[5 empty] | Efficiency – losses¦REVIEW | Where will we lose material, conversion, yield or energy?
[5 empty] | Construction¦REVIEW | Demolition
[5 empty] | Construction¦REVIEW | Impacts on existing site, existing operations and environment
[5 empty] | Construction¦REVIEW | Size of equipment
[5 empty] | Construction¦REVIEW | Special hazards – chemicals / dangerous goods, to workers, structural
[5 empty] | Construction¦REVIEW | Personal protective equipment
[5 empty] | Commissioning¦REVIEW | Broadly how it will be done
[5 empty] | Commissioning¦REVIEW | Sequence
[5 empty] | Commissioning¦REVIEW | What difficulties and hazards can be foreseen
[5 empty] | Commissioning¦REVIEW | Review of procedures
[5 empty] | Commissioning¦REVIEW | Signage / tags / locks
[5 empty] | Commissioning¦REVIEW | Responsibilities
[5 empty] | Commissioning¦REVIEW | [S] Refractory dry-out and first heat
[5 empty] | Start-up¦REVIEW | First start-up methods, difficulties, hazards
[5 empty] | Start-up¦REVIEW | Routine start-up methods, difficulties, hazards
[5 empty] | Start-up¦REVIEW | Philosophy of control (auto, manual, local)
[5 empty] | Start-up¦REVIEW | Too many interlocks?
[5 empty] | Start-up¦REVIEW | Procedures
[5 empty] | Start-up¦REVIEW | Purging and gas-freeing before light-up
[5 empty] | Shutdown (isolation, purging)¦REVIEW | Planned shutdown
[5 empty] | Shutdown (isolation, purging)¦REVIEW | Emergency shutdown
[5 empty] | Shutdown (isolation, purging)¦REVIEW | Difficulties, hazards
[5 empty] | Shutdown (isolation, purging)¦REVIEW | [S] Holding molten metal during an extended stop; emptying furnaces and ladles
[5 empty] | Breakdown (including service failure)¦REVIEW | Power failure
[5 empty] | Breakdown (including service failure)¦REVIEW | Air, steam, water, vacuum, fuel
[5 empty] | Breakdown (including service failure)¦REVIEW | Vents
[5 empty] | Breakdown (including service failure)¦REVIEW | Computer
[5 empty] | Breakdown (including service failure)¦REVIEW | Other
[5 empty] | Breakdown (including service failure)¦REVIEW | Major causes of breakdown
[5 empty] | Breakdown (including service failure)¦REVIEW | Emergency procedures and communications
[5 empty] | Breakdown (including service failure)¦REVIEW | Which way should valves move (fail-safe positions)?
[5 empty] | Materials¦REVIEW | Vessels
[5 empty] | Materials¦REVIEW | Pipelines
[5 empty] | Materials¦REVIEW | Pumps
[5 empty] | Materials¦REVIEW | Valves
[5 empty] | Materials¦REVIEW | Gaskets / seals
[5 empty] | Materials¦REVIEW | Protective coatings
[5 empty] | Materials¦REVIEW | Others (refractory, copper, hoses)
[5 empty] | Utilities and services¦REVIEW | Lighting
[5 empty] | Utilities and services¦REVIEW | Compressed air; instrument air
[5 empty] | Utilities and services¦REVIEW | Nitrogen
[5 empty] | Utilities and services¦REVIEW | Water (cooling, process, service, potable)
[5 empty] | Utilities and services¦REVIEW | Steam
[5 empty] | Utilities and services¦REVIEW | Power
[5 empty] | Utilities and services¦REVIEW | Oxygen
[5 empty] | Toxicity¦REVIEW | Material safety data sheets
[5 empty] | Toxicity¦REVIEW | Handling procedures
[5 empty] | Toxicity¦REVIEW | Precautions
[5 empty] | Toxicity¦REVIEW | Exposure monitoring
[5 empty] | Toxicity¦REVIEW | Emergency procedures
[5 empty] | Toxicity¦REVIEW | Ventilation
[5 empty] | Toxicity¦REVIEW | [S] CO, metal fume, silica, PAHs from coke and pitch
[5 empty] | Fire and explosion¦REVIEW | Broad overview
[5 empty] | Fire and explosion¦REVIEW | Protection, prevention, control
[5 empty] | Fire and explosion¦REVIEW | Location of safety showers, deluges
[5 empty] | Fire and explosion¦REVIEW | Location of shut-off valves and controls
[5 empty] | Fire and explosion¦REVIEW | [S] Molten metal explosions, dust explosions, gas explosions, hydraulic oil fires
[5 empty] | Environmental impact¦REVIEW | Vapour emissions
[5 empty] | Environmental impact¦REVIEW | Dust emissions
[5 empty] | Environmental impact¦REVIEW | Effluent
[5 empty] | Environmental impact¦REVIEW | Noise
[5 empty] | Environmental impact¦REVIEW | Ground seepage
[5 empty] | Environmental impact¦REVIEW | Waste minimisation
[5 empty] | Environmental impact¦REVIEW | [S] Slag, mill scale, sludge, EAF dust disposal
[5 empty] | Natural hazards¦REVIEW | Earthquake
[5 empty] | Natural hazards¦REVIEW | Flooding
[5 empty] | Natural hazards¦REVIEW | Thunderstorm (lightning protection)
[5 empty] | Natural hazards¦REVIEW | High winds
[5 empty] | Natural hazards¦REVIEW | Sandstorms; extreme heat
[5 empty] | Quality and consistency¦REVIEW | What will most cause quality to fail or vary?
[5 empty] | Quality and consistency¦REVIEW | How to prevent it
[5 empty] | Procedures – development and documentation¦REVIEW | Operations
[5 empty] | Procedures – development and documentation¦REVIEW | Maintenance
[5 empty] | Procedures – development and documentation¦REVIEW | Confined space
[5 empty] | Procedures – development and documentation¦REVIEW | Inspection and testing
[5 empty] | Procedures – development and documentation¦REVIEW | Emergency
[5 empty] | Procedures – development and documentation¦REVIEW | Engineering drawings
[5 empty] | Safety equipment¦REVIEW | Personal protective equipment (PPE)
[5 empty] | Safety equipment¦REVIEW | Fire detection
[5 empty] | Safety equipment¦REVIEW | Fire fighting
[5 empty] | Safety equipment¦REVIEW | Means of escape
[5 empty] | Safety equipment¦REVIEW | Gas monitors
[5 empty] | Safety equipment¦REVIEW | Breathing apparatus
[5 empty] | Safety equipment¦REVIEW | Safety shower
[5 empty] | Safety equipment¦REVIEW | Barriers / guards
[5 empty] | Safety equipment¦REVIEW | [S] Heat-protective clothing; molten-metal splash protection
[5 empty] | Egress / access¦REVIEW | Number of exit points
[5 empty] | Egress / access¦REVIEW | Emergency egress
[5 empty] | Egress / access¦REVIEW | Size – width, height, length
[5 empty] | Egress / access¦REVIEW | Obstructions
[5 empty] | Egress / access¦REVIEW | Lighting
[5 empty] | Egress / access¦REVIEW | Fire protection
[5 empty] | Entry / exit points¦REVIEW | Location
[5 empty] | Entry / exit points¦REVIEW | Arrangement
[5 empty] | Entry / exit points¦REVIEW | Communications
[5 empty] | Entry / exit points¦REVIEW | External impacts
[5 empty] | Layout and facility siting¦REVIEW | Spacing between hazardous units
[5 empty] | Layout and facility siting¦REVIEW | Occupied buildings near hazards
[5 empty] | Layout and facility siting¦REVIEW | Vehicle routes near molten metal or gas mains
[5 empty] | Layout and facility siting¦REVIEW | Simultaneous operations (SIMOPS)

## Risk Matrix
RISK MATRIX (5 x 5)
Risk score = value in the matrix cell for Severity (row) x Likelihood (column). Default scores are S x L (1–25); overwrite the yellow cells to use your company's matrix.
LIKELIHOOD →
| Severity \ Likelihood | 1 – Rare | 2 – Unlikely | 3 – Possible | 4 – Likely | 5 – Almost certain
SEVERITY ↓ | 5 – Catastrophic | 5 | 10 | 15 | 20 | 25
| 4 – Major | 4 | 8 | 12 | 16 | 20
| 3 – Moderate | 3 | 6 | 9 | 12 | 15
| 2 – Minor | 2 | 4 | 6 | 8 | 10
| 1 – Negligible | 1 | 2 | 3 | 4 | 5
Risk bands (minimum score):
| Low | 1 | Tolerable – manage by procedures
| Medium | 5 | Tolerable if ALARP – review safeguards
| High | 10 | Recommendation required to reduce risk
| Very High | 20 | Intolerable – mandatory risk reduction
| Severity level | People | Environment | Asset / production
| 1 – Negligible | First aid case; no lost time | Minor release contained on site; no impact | Negligible damage / production loss
| 2 – Minor | Medical treatment case / restricted work | Reportable release, contained on site, short-term impact | Minor damage; short production loss
| 3 – Moderate | Lost-time injury; reversible health effect | Off-site release with short-term impact | Significant damage; production loss of days
| 4 – Major | Single fatality or permanent disability | Off-site release with significant medium-term impact | Major damage; extended production loss
| 5 – Catastrophic | Multiple fatalities; off-site injuries | Major off-site release; long-term environmental damage | Loss of unit / plant; extended outage
| Likelihood level | Description
| 1 – Rare | Not expected to occur in the life of the facility (< 1 in 10 000 years)
| 2 – Unlikely | Has occurred in the industry; not expected here (1 in 1 000 – 10 000 years)
| 3 – Possible | Could occur in the life of the facility (1 in 100 – 1 000 years)
| 4 – Likely | Expected to occur several times in the life of the facility (1 in 10 – 100 years)
| 5 – Almost certain | Expected to occur within the year (> 1 in 10 years)
Descriptors and frequencies are typical examples – replace with the client's approved risk matrix before the study.
Note on C12: Band thresholds are editable inputs (default for S x L matrix). Align with your company risk standard.

## Node 01
HAZOP WORKSHEET
Select node ▸ |  |  | N01 – Gas receiving & metering station (GRMS) | [8 empty] | Session date | 2026-10-12 |  | Revision | A
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by
| Flow | NO |  | Supplier pipeline trip / supplier ESD | Spurious closure of ESDV-1001 (solenoid, power or air failure) | Both filter-separators F-1002A/B blocked (black powder) |  |  |  |  | Loss of gas to all users: reformer, reheat furnace, preheater and oxy-fuel burner flame-outs and trips; on uncontrolled restoration of supply, gas may enter burners that are not proven shut – accumulation and explosion on relight (see N06-01); production loss [N01-01] Restoration after an interruption is the hazardous phase – see N06 and R-006. | 3 – Moderate | 3 – Possible |  |  | PSLL-2006 / PSLL-4005 – Low-low gas pressure trips in the user burner management systems (reformer, reheat furnace, preheaters) | Yes | F-1002A/B – Duty / standby filter-separators with LSH-1002 high-liquid alarm and PDIT-1002 differential-pressure alarm | No | Gas supply agreement quality specification; supplier notification of off-spec gas and supply interruptions | No | [8 empty] | 3 – Moderate | 2 – Unlikely |  |  | R-006 Agree a supply-interruption and restoration protocol with the gas supplier: users isolated before re-pressurisation, controlled restoration sequence, BMS re-start only after confirmed header pressure. | Utilities manager
| Pressure | MORE |  | Failed-open pressure control valves (PCVs) | Supplier pressure excursion above normal operating range | Thermal expansion of trapped (blocked-in) liquid |  |  |  |  | Overpressure of filter-separators / meter runs only if their design pressure were below the pipeline MAOP; blocked-in sections heated by the sun – flange leak, release of high-pressure gas (bow tie BT-GN-01) [N01-02] GRMS designed for the pipeline MAOP (50 barg) – overpressure from the supplier not credible. | 5 – Catastrophic | 2 – Unlikely |  |  | GRMS piping, filter-separators and meter runs designed for the pipeline MAOP (no overpressure from the supplier) | Yes | PSV-1006A/B – Filter-separator fire-case / thermal relief valves | Yes | PT-1005 – GRMS inlet pressure high alarm PAH-1005 with operator response | No | [8 empty] | 5 – Catastrophic | 1 – Rare
| Flow | AS WELL AS |  | Gas or air entrainment in liquid; liquid carry-over in gas | Pigging debris and black powder from the supplier pipeline | Condensate from the pipeline after cold weather / pigging |  |  |  |  | Filter-separator overload; liquid / dust carry-over to meters and regulator pilots – active regulator may stick open (demand on overpressure protection, N02-02); erosion; liquid slugs cause flame instability at burners [N01-03] Carry-over is one of the initiating causes in fault tree FT-GN-01 (active regulator fails open). | 4 – Major | 3 – Possible |  |  | F-1002A/B – Duty / standby filter-separators with LSH-1002 high-liquid alarm and PDIT-1002 differential-pressure alarm | No | Operator rounds with portable gas detector; annual acoustic leak survey | No | [10 empty] | 4 – Major | 2 – Unlikely |  |  | R-016 Route the filter-separator drains to a closed drain vessel instead of an open drain; review the LSH-1002 alarm response. | Process engineer
| Composition | OTHER THAN |  | Wrong raw material delivered or unloaded | H2S / higher hydrocarbons above the supply specification | Wobbe index change (supplier gas source change) |  |  |  |  | H2S poisons the DRI reformer catalyst and is toxic on release; Wobbe index change alters burner heat release – over-firing or flame instability in the reheat furnace and preheaters [N01-04] Composition is also reviewed for the DRI plant in N04-04. | 3 – Moderate | 3 – Possible |  |  | AT-1004 – Gas chromatograph – composition, Wobbe index and H2S monitoring with alarm | No | Gas supply agreement quality specification; supplier notification of off-spec gas and supply interruptions | No | [10 empty] | 3 – Moderate | 2 – Unlikely
| Process gas (CO, H2 – BFG, COG, LD gas, reducing gas) | LEAK OF |  | Flange, valve or seal leak; water-seal blown | Small-bore fitting fatigue (meter-run vibration) | Pig receiver closure opened or leaking under pressure |  |  |  |  | High-pressure natural gas release fed from the pipeline inventory: jet fire if ignited immediately; flash fire or vapour cloud explosion if ignited later – potential multiple fatalities and loss of gas to the whole works (event tree ETA-GN-01) [N01-05] Quantified: bow tie BT-GN-01 (top event = loss of containment of the HP / MP system), event tree ETA-GN-01 (initiating event = BT-GN-01 top), fault tree FT-GN-02 (ESD). Likelihood after safeguards from the calculated frequency 4.3E-6 /yr. | 5 – Catastrophic | 3 – Possible |  |  | UCP-1000 – Gas detection GD-1110A/B/C (2oo3) and ESD isolation of the HP / MP system – ESDV-1001 and ESDV-1107 close (SIS UCP-1000) | Yes | Ignition source control – hazardous area classification with Ex equipment, hot-work permit, vehicle control | No | PR-1001 – Pig receiver quick-opening closure with pressure-warning / locking device (key interlock with vent valve) | Yes | Separation distances and fire-proofing of supports in the GRMS / PRS | No | Emergency response team / fire brigade; emergency response plan for gas releases and fires | No |  |  |  |  | 5 – Catastrophic | 1 – Rare |  |  | R-001 Verify the HP / MP gas detection & ESD function against the required risk reduction. Fault tree FT-GN-02 gives PFDavg 2.6E-2 (RRF 38); test the effect of six-monthly partial-stroke testing of ESDV-1001 / ESDV-1107 and quarterly detector bump tests (FMECA S01 / S08). R-017 Verify the pig-receiver quick-opening closure safety device (pressure-warning / key interlock with the vent valve) and include it in the pigging procedure and its training. R-021 Assess the vapour cloud explosion overpressure at the PRS / GRMS and verify the siting of the utilities control room (bow tie BT-GN-01 / event tree ETA-GN-01 VCE end state). | Instrument engineer / Mechanical engineer / HSE / process safety
| Corrosion / erosion | MORE |  | Cathodic protection arrangements inadequate | Insulating joint IJ-1001 shorted (debris, bonding cable) | Coating damage at road crossings |  |  |  |  | Wall loss leading to a leak or rupture of the buried section – gas migrates through soil into trenches / buildings (bow tie BT-GN-01 threat 2) [N01-06] FMECA S03 CP-1200; bow tie BT-GN-01 threat T2. | 5 – Catastrophic | 3 – Possible |  |  | CP-1200 – Coating and impressed-current cathodic protection of buried sections; annual CP / DCVG survey | No | Piping inspection programme – thickness monitoring at supports, rack crossings and low points | No | [10 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-008 Survey stray currents and induced voltages on gas pipework near the EAF / LF high-current systems; verify insulating joints and bonding; include in CP interference testing. | Electrical engineer
| Maintenance | INADEQUATE |  | Isolation, drainage, purging | Pig receiver opened before full depressurisation | Work permit system |  |  |  |  | Pig receiver door blown open or gas release onto the operator; pyrophoric iron sulphide in pig debris ignites on exposure to air [N01-07] Bow tie BT-GN-01 threat T5 (maintenance error). | 5 – Catastrophic | 3 – Possible |  |  | PR-1001 – Pig receiver quick-opening closure with pressure-warning / locking device (key interlock with vent valve) | Yes | Pigging procedure OP-GN-010: depressurise, N2 purge and gas test before opening the pig receiver | No | Permit-to-work with isolation verification (DBB / spades), gas-free test and fire watch | No | [8 empty] | 5 – Catastrophic | 1 – Rare |  |  | R-017 Verify the pig-receiver quick-opening closure safety device (pressure-warning / key interlock with the vent valve) and include it in the pigging procedure and its training. | Mechanical engineer

## Node 02
HAZOP WORKSHEET
Select node ▸ |  |  | N02 – Gas heaters H-1101A/B and pressure reduction station PRS-1 | [8 empty] | Session date | 2026-10-12 |  | Revision | A
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by
| Temperature | LESS |  | Heater H-1101A trip (flame failure, low bath level) | Heater undersized at peak flow / TIC-1101 fault | Reducing pressure (auto-refrigeration of LPG, CO2, ammonia) |  |  |  |  | Joule–Thomson cooling (~0.5 °C per bar, ~17 °C for 42 → 7 barg) – outlet below 0 °C: hydrate / ice in regulator pilots (active regulator may fail open – demand on N02-02 protection); piping below its MDMT – brittle fracture [N02-01] Ice in the pilot is an initiating cause in fault tree FT-GN-01 (BE-001). | 4 – Major | 3 – Possible |  |  | H-1101A/B – Duty / standby water-bath gas heaters with outlet temperature control TIC-1101 | No | TT-1101 – Low gas outlet temperature alarm TSL-1101 (+5 °C) with operator response | No | H-1101A/B – Heater burner management: flame failure, low bath level LSLL and high bath temperature TSHH trips | No | [8 empty] | 4 – Major | 2 – Unlikely |  |  | R-004 Confirm the minimum PRS outlet gas temperature against the MDMT of the downstream piping; add automatic change-over to the standby heater on TSL-1101 and an alarm on heater trip. | Process engineer
| Pressure | MORE |  | Failed-open pressure control valves (PCVs) | Regulator sensing line blocked or isolated | Ice / debris in the active regulator pilot |  |  |  |  | Overpressure of the whole MP network (inlet up to 42 barg vs 10 barg design): flange leaks and possible rupture across the site, overpressure of district stations and burner trains – fires / explosions at several locations [N02-02] Quantified: fault tree FT-GN-01 – top = MP header overpressure 3.6E-5 /yr; gate G-002 (monitor + slam-shut) PFDavg 2.0E-4; bow tie BT-GN-01 threat T1. PSV-1105 is a token relief and is not credited. Likelihood after safeguards from the calculated frequency 3.6E-5 /yr. | 5 – Catastrophic | 4 – Likely |  |  | PCV-1103A/B – Monitor regulator takes over on active-regulator failure (set 7.5 barg) | Yes | SSV-1102A/B – Slam-shut valve with over-pressure shut-off (OPSO 8.5 barg) on each regulator run | Yes | PSV-1105 – Token relief valve (9.0 barg) to VS-1301 – lock-up creep / small leaks only, not sized for full regulator failure | No | PT-1106 – PRS outlet high-pressure alarm PAH-1106 (7.8 barg) with operator response | No | Regulator-run bypass valves car-sealed / locked closed (CSC register) | No |  |  |  |  | 5 – Catastrophic | 1 – Rare |  |  | R-002 Confirm and record PRS-1 set-point staggering (active 7.0 / monitor 7.5 / SSV OPSO 8.5 / PSV-1105 9.0 barg; MP design 10 barg) in the PRS data sheet; add the regulator-run bypass valves to the car-seal (CSC) register. R-003 Introduce an annual lock-up / take-over test of monitor regulators PCV-1103A/B and a six-monthly trip test of slam-shut valves SSV-1102A/B – these intervals are the basis of fault tree FT-GN-01 (protection PFDavg 2.0E-4). | Process engineer / Instrument engineer
| Pressure | LESS |  | Slam-shut SSV-1102A spurious trip | Active and monitor regulators fail closed / filter blocked | Hydrate in regulator pilot |  |  |  |  | Low header pressure: flame-out at reheat furnace, preheaters and reformer burners; danger on relight if the burner shut-off is not proven (see N06) [N02-03] Run B takes over automatically if run A closes. | 3 – Moderate | 3 – Possible |  |  | Standby regulator run B on automatic (set 0.3 bar lower) – takes over if run A closes | No | PSLL-2006 / PSLL-4005 – Low-low gas pressure trips in the user burner management systems (reformer, reheat furnace, preheaters) | Yes | PT-1210 – MP header low-pressure alarm PAL-1210 (leak / supply-loss indication) | No | [8 empty] | 3 – Moderate | 2 – Unlikely |  |  | R-006 Agree a supply-interruption and restoration protocol with the gas supplier: users isolated before re-pressurisation, controlled restoration sequence, BMS re-start only after confirmed header pressure. | Utilities manager
| Flow | MORE |  | Control faults – control valve fails open, bypass left open, wrong set point | All users at maximum firing during DRI module start-up | [5 empty] | Regulators fully open, outlet pressure sags, extra Joule–Thomson cooling, high velocity – noise, erosion and vibration of regulator runs [N02-04] Operability issue – capacity check in the design basis. | 2 – Minor | 3 – Possible |  |  | Standby regulator run B on automatic (set 0.3 bar lower) – takes over if run A closes | No | PT-1210 – MP header low-pressure alarm PAL-1210 (leak / supply-loss indication) | No | [10 empty] | 2 – Minor | 2 – Unlikely
| Process gas (CO, H2 – BFG, COG, LD gas, reducing gas) | LEAK OF |  | Flange, valve or seal leak; water-seal blown | Regulator diaphragm rupture venting through the pilot vent | Gas detection inoperative or poorly located |  |  |  |  | Gas accumulates in the partly enclosed shelter – confined explosion; jet fire on the regulator runs (event tree ETA-GN-01) [N02-05] Bow tie BT-GN-01 threat T6; event tree ETA-GN-01. Likelihood after safeguards from the calculated frequency 4.3E-6 /yr. | 5 – Catastrophic | 3 – Possible |  |  | VS-1301 – Regulator pilot / diaphragm vents and PSV discharges piped to vent stack VS-1301 outside the PRS shelter | No | PRS shelter natural ventilation (louvres at high and low level) | No | UCP-1000 – Gas detection GD-1110A/B/C (2oo3) and ESD isolation of the HP / MP system – ESDV-1001 and ESDV-1107 close (SIS UCP-1000) | Yes | Ignition source control – hazardous area classification with Ex equipment, hot-work permit, vehicle control | No | [6 empty] | 5 – Catastrophic | 1 – Rare |  |  | R-001 Verify the HP / MP gas detection & ESD function against the required risk reduction. Fault tree FT-GN-02 gives PFDavg 2.6E-2 (RRF 38); test the effect of six-monthly partial-stroke testing of ESDV-1001 / ESDV-1107 and quarterly detector bump tests (FMECA S01 / S08). R-005 Route all regulator pilot / diaphragm vents and the PSV-1105 discharge to vent stack VS-1301 outside the PRS shelter; confirm by dispersion check that the vent is clear of heater flues and platforms. | Instrument engineer / Process engineer
| Temperature | MORE |  | Defective control (TIC fault, heater fails on) | Low bath level (evaporation, leak) | Gas coil leak into the water bath |  |  |  |  | Fire-tube overheating and failure – heater fire; a gas-coil leak vents gas through the bath vent next to the firebox – fire / explosion at the heater [N02-06] FMECA S02 H-1101A. | 4 – Major | 3 – Possible |  |  | H-1101A/B – Heater burner management: flame failure, low bath level LSLL and high bath temperature TSHH trips | Yes | Operator rounds with portable gas detector; annual acoustic leak survey | No | [10 empty] | 4 – Major | 2 – Unlikely |  |  | R-004 Confirm the minimum PRS outlet gas temperature against the MDMT of the downstream piping; add automatic change-over to the standby heater on TSL-1101 and an alarm on heater trip. | Process engineer
| Relief | INADEQUATE |  | Relief philosophy not defined for all scenarios (fire, blocked outlet, runaway, tube rupture) | Relief valve discharge location unsafe (to work areas, ignition sources) | [5 empty] | PSV-1105 is a token relief – full-flow regulator failure relies on the monitor regulator and slam-shut; vent discharge near the heaters could ignite [N02-07] Accepted design practice for gas pressure regulating stations: two independent overpressure protections instead of full-flow relief. | 5 – Catastrophic | 2 – Unlikely |  |  | PCV-1103A/B – Monitor regulator takes over on active-regulator failure (set 7.5 barg) | Yes | SSV-1102A/B – Slam-shut valve with over-pressure shut-off (OPSO 8.5 barg) on each regulator run | Yes | VS-1301 – Vent stack VS-1301 3 m above the nearest platform, away from heater flues; N2 snuffing | No | [8 empty] | 5 – Catastrophic | 1 – Rare |  |  | R-002 Confirm and record PRS-1 set-point staggering (active 7.0 / monitor 7.5 / SSV OPSO 8.5 / PSV-1105 9.0 barg; MP design 10 barg) in the PRS data sheet; add the regulator-run bypass valves to the car-seal (CSC) register. R-005 Route all regulator pilot / diaphragm vents and the PSV-1105 discharge to vent stack VS-1301 outside the PRS shelter; confirm by dispersion check that the vent is clear of heater flues and platforms. | Process engineer

## Node 03
HAZOP WORKSHEET
Select node ▸ |  |  | N03 – MP ring main (7 barg) and pipe racks | [8 empty] | Session date | 2026-10-12 |  | Revision | A
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by
| Process gas (CO, H2 – BFG, COG, LD gas, reducing gas) | LEAK OF |  | Flange, valve or seal leak; water-seal blown | Mechanical impact by mobile cranes / vehicles at rack crossings | External corrosion of buried crossings or at pipe supports | Third-party excavation |  |  |  | Release in congested plant areas (melt shop, rolling mill): jet fire or vapour cloud explosion; gas migrating into cable trenches and building HVAC intakes – explosion inside buildings [N03-01] Bow tie BT-GN-01 threats T2 (corrosion), T3 (impact), T4 (flange / fitting failure). | 5 – Catastrophic | 3 – Possible |  |  | CP-1200 – Coating and impressed-current cathodic protection of buried sections; annual CP / DCVG survey | No | Crash barriers and height gantries at pipe-rack road crossings; lift plans for cranes near racks | No | Ground-disturbance / excavation permit with buried-services drawing | No | PT-1210 – MP header low-pressure alarm PAL-1210 (leak / supply-loss indication) | No | XV-1201…1204 – Remote-operated sectionalising valves on the MP ring main | No | Ignition source control – hazardous area classification with Ex equipment, hot-work permit, vehicle control | No |  |  | 5 – Catastrophic | 2 – Unlikely |  |  | R-007 Install gas detection at the HVAC intakes and cable-trench entries of buildings near the MP header (substations, control rooms) with HVAC trip. R-009 Include buried gas-line routes in the ground-disturbance permit; mark crossings on site; review crash protection and height gantries at pipe-rack road crossings. | HSE / process safety / Civil engineer
| Pressure | MORE |  | Failed-open pressure control valves (PCVs) | Leakage from interconnected high-pressure system | [5 empty] | As N02-02 – whole MP network above its 10 barg design pressure [N03-02] Covered by N02-02 and fault tree FT-GN-01; recorded here so the node is complete. Likelihood after safeguards from the calculated frequency 3.6E-5 /yr. | 5 – Catastrophic | 4 – Likely |  |  | PCV-1103A/B – Monitor regulator takes over on active-regulator failure (set 7.5 barg) | Yes | SSV-1102A/B – Slam-shut valve with over-pressure shut-off (OPSO 8.5 barg) on each regulator run | Yes | [10 empty] | 5 – Catastrophic | 1 – Rare |  |  | R-003 Introduce an annual lock-up / take-over test of monitor regulators PCV-1103A/B and a six-monthly trip test of slam-shut valves SSV-1102A/B – these intervals are the basis of fault tree FT-GN-01 (protection PFDavg 2.0E-4). | Instrument engineer
| Air / oxygen in process gas | AS WELL AS |  | Inadequate purging at start-up / shutdown | Air ingress through leaks at negative pressure | [5 empty] | Flammable gas / air mixture inside the header on gas-in – internal deflagration, flashback at the first burner lit [N03-03] See N07-01. | 5 – Catastrophic | 2 – Unlikely |  |  | Written purge plan OP-GN-020: N2 purge to O2 < 2 % before gas-in and gas > 90 % at the vent before relight (portable analyser) | No | Valve line-up checklist and spectacle-blind register | No | [10 empty] | 5 – Catastrophic | 1 – Rare |  |  | R-015 Purge plan for every gas-in / gas-out: N2 purge with O2 < 2 % confirmed before gas-in and gas > 90 % confirmed at the vent before relight; calibrated portable analysers. | Operations superintendent
| Corrosion / erosion | MORE |  | Internal / external corrosion protection | Corrosion at pipe supports on the racks | Cathodic protection arrangements inadequate |  |  |  |  | Wall loss – leak (as N03-01) [N03-04] FMECA S03 L-1200 and CP-1200. | 5 – Catastrophic | 3 – Possible |  |  | CP-1200 – Coating and impressed-current cathodic protection of buried sections; annual CP / DCVG survey | No | Piping inspection programme – thickness monitoring at supports, rack crossings and low points | No | [10 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-009 Include buried gas-line routes in the ground-disturbance permit; mark crossings on site; review crash protection and height gantries at pipe-rack road crossings. | Civil engineer
| Electrical safety / static | INADEQUATE |  | EAF / LF high-current systems inducing voltages on nearby pipework | Insulating joints bypassed; lightning | [5 empty] | Arcing at flanges during maintenance – ignition of a gas release; accelerated stray-current corrosion of buried sections [N03-05] Steel-works specific – see FMECA S03. | 4 – Major | 3 – Possible |  |  | Bonding / earthing of pipe racks, lightning protection and insulating joints at building entries | No | CP-1200 – Coating and impressed-current cathodic protection of buried sections; annual CP / DCVG survey | No | [10 empty] | 4 – Major | 2 – Unlikely |  |  | R-008 Survey stray currents and induced voltages on gas pipework near the EAF / LF high-current systems; verify insulating joints and bonding; include in CP interference testing. | Electrical engineer
| Operator action | OTHER THAN |  | Isolation in error (wrong valve closed, LOTO on wrong equipment) | Valve line-up not checked | [5 empty] | Loss of gas to a whole plant area – flame-outs (as N02-03); maintenance on a section believed isolated but still live [N03-06] | 4 – Major | 3 – Possible |  |  | Valve line-up checklist and spectacle-blind register | No | Permit-to-work with isolation verification (DBB / spades), gas-free test and fire watch | No | PSLL-2006 / PSLL-4005 – Low-low gas pressure trips in the user burner management systems (reformer, reheat furnace, preheaters) | Yes | [8 empty] | 4 – Major | 2 – Unlikely

## Node 04
HAZOP WORKSHEET
Select node ▸ |  |  | N04 – DRI plant gas supply – district station DS-2 | [8 empty] | Session date | 2026-10-13 |  | Revision | A
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by
| Flow | MORE |  | [S] Excess fuel gas to reheat furnace, ladle pre-heater or stove burners | FCV-2004 fails open | [5 empty] | Reformer over-firing: tube overheating and rupture – reducing-gas fire in the reformer box; CO in the flue gas [N04-01] FMECA S04 FCV-2004; reformer covered in detail by the DRI plant HAZOP. | 4 – Major | 3 – Possible |  |  | Reformer burner management – high fuel flow and high tube-wall temperature trips | Yes | Cross-limited air / fuel ratio control | No | [10 empty] | 4 – Major | 2 – Unlikely
| Flow | NO |  | Equipment failure – control valve fails closed, isolation valve, pump or compressor trip, vessel failure | ESDV-2001 spurious closure | [5 empty] | Reformer flame-out and DRI module trip; loss of reducing gas quality; production loss [N04-02] | 3 – Moderate | 3 – Possible |  |  | PSLL-2006 / PSLL-4005 – Low-low gas pressure trips in the user burner management systems (reformer, reheat furnace, preheaters) | Yes | [12 empty] | 3 – Moderate | 2 – Unlikely
| Flow | REVERSE |  | Defective or passing non-return valve | Two-way flow in common headers | Low NG pressure at the make-up point (supply loss) |  |  |  |  | H2 / CO-rich reducing gas flows back into the NG system – CO toxic exposure at other users' burners and vents, flame instability [N04-03] FMECA S04 XV-2008 (hidden failure – passing in the closed position). | 5 – Catastrophic | 3 – Possible |  |  | XV-2008 – Double non-return valves + XV-2008 closes on low NG / process-gas differential pressure PDALL-2009 | Yes | [12 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-018 Provide reverse-flow protection at the DRI process-gas NG make-up point: double check valves plus a PDALL-2009 trip closing XV-2008; annual reverse-flow leak test. | DRI process engineer
| Composition | AS WELL AS |  | [S] Hydrogen, CO or H2S in process gas above design values | Black powder carry-over from the GRMS | [5 empty] | Reformer catalyst poisoning; fouling of burner nozzles [N04-04] See N01-04. | 3 – Moderate | 3 – Possible |  |  | AT-1004 – Gas chromatograph – composition, Wobbe index and H2S monitoring with alarm | No | F-1002A/B – Duty / standby filter-separators with LSH-1002 high-liquid alarm and PDIT-1002 differential-pressure alarm | No | [10 empty] | 3 – Moderate | 2 – Unlikely
| Pressure | MORE |  | Failed-open pressure control valves (PCVs) | [6 empty] | Downstream piping exposed to full MP pressure (7 barg) – within its 10 barg design; burner pressure high, trip on high pressure [N04-05] Inherently safe – downstream designed for MP pressure. | 2 – Minor | 3 – Possible |  |  | District-station downstream piping designed for full MP header pressure (10 barg) | Yes | Reformer burner management – high fuel flow and high tube-wall temperature trips | No | [10 empty] | 2 – Minor | 2 – Unlikely

## Node 05
HAZOP WORKSHEET
Select node ▸ |  |  | N05 – Melt shop gas supply – DS-3, EAF oxy-fuel burners and ladle preheaters | [8 empty] | Session date | 2026-10-13 |  | Revision | A
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by
| Oxygen (lances, burners, pipelines) | AS WELL AS |  | Burner flame-out with continued fuel supply | O2 back-flow through the burner when NG pressure is lost | Defective or passing non-return valve |  |  |  |  | Explosive NG / O2 mixture inside the NG line – flashback, detonation in the burner line, fire in the melt shop next to the EAF [N05-01] FMECA S05 NRV-3010 (hidden failure). | 5 – Catastrophic | 3 – Possible |  |  | NRV-3010 – Non-return valves and flashback arrestors on the NG and O2 lines at each oxy-fuel burner and preheater | Yes | XV-3011 – Burner management: O2 and NG shut off on low NG pressure PSLL-3012; N2 purge of burner after shutdown | Yes | [10 empty] | 5 – Catastrophic | 1 – Rare |  |  | R-013 Fit / verify non-return valves and flashback arrestors on the NG and O2 lines at every EAF oxy-fuel burner and ladle preheater; prove the 'low NG pressure closes O2' interlock annually. | Melt shop maintenance
| Process gas (CO, H2 – BFG, COG, LD gas, reducing gas) | LEAK OF |  | Flange, valve or seal leak; water-seal blown | Molten-metal splash / radiant heat damaging NG hoses near the EAF | Confined spaces near gas mains |  |  |  |  | Immediate ignition near molten metal – fire on the burner skid; gas in basements / cable tunnels – explosion [N05-02] | 4 – Major | 3 – Possible |  |  | Heat shields and routing of NG lines away from molten-metal splash zones; hose inspection | No | XV-3011 – Burner management: O2 and NG shut off on low NG pressure PSLL-3012; N2 purge of burner after shutdown | Yes | Operator rounds with portable gas detector; annual acoustic leak survey | No | [8 empty] | 4 – Major | 2 – Unlikely |  |  | R-007 Install gas detection at the HVAC intakes and cable-trench entries of buildings near the MP header (substations, control rooms) with HVAC trip. R-019 Heat-shield and re-route NG lines and hoses near the EAF and ladle area; six-monthly hose inspection and replacement on condition. | HSE / process safety / Melt shop maintenance
| Pressure | LESS |  | [S] Low fuel-gas pressure at burners (flame-out followed by re-ignition of accumulated gas) | DS-3 regulator / SSV-3003 trip | [5 empty] | Flame-out at the preheater; gas accumulates in the ladle / tundish – explosion on relight [N05-03] Same mechanism as N06-01 (smaller inventory). | 4 – Major | 3 – Possible |  |  | LPH-3020 – Ladle preheater burner management – UV flame scanner, flame-failure shut-off, pre-purge timer | Yes | [12 empty] | 4 – Major | 2 – Unlikely |  |  | R-012 Bypass / override management for BMS, SIS and gas detectors: authorisation, time limit, logging and monthly audit; BMS logic changes only under MOC. | HSE / process safety
| Operator action | OTHER THAN |  | Auto / manual facility and human error | Alarm flooding; bypassed trips | [5 empty] | Gas accumulation and explosion in the ladle; burns to the operator [N05-04] PHBMS not credited as an IPL here because the cause is its bypass. | 4 – Major | 3 – Possible |  |  | LPH-3020 – Ladle preheater burner management – UV flame scanner, flame-failure shut-off, pre-purge timer | No | Bypass / override management – authorised, time-limited, logged; monthly audit | No | [10 empty] | 4 – Major | 2 – Unlikely |  |  | R-012 Bypass / override management for BMS, SIS and gas detectors: authorisation, time limit, logging and monthly audit; BMS logic changes only under MOC. | HSE / process safety

## Node 06
HAZOP WORKSHEET
Select node ▸ |  |  | N06 – Rolling-mill reheat furnace fuel gas train and burner management | [8 empty] | Session date | 2026-10-14 |  | Revision | A
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by
| Flow | NO |  | Burner flame-out with continued fuel supply | [S] Low fuel-gas pressure at burners (flame-out followed by re-ignition of accumulated gas) | Failed light-off of a main burner |  |  |  |  | Unburnt gas enters a furnace zone below auto-ignition temperature (start-up / low fire) – explosive mixture, furnace explosion: casing / door failure, fatalities on the furnace platforms [N06-01] Quantified: fault tree FT-GN-03 (BMS flame-failure shut-off PFDavg 1.1E-2; top 9.2E-3 /yr), event tree ETA-GN-02 (explosion 9.2E-4 /yr vs target 1E-4), bow tie BT-GN-02 threat T1. Likelihood after safeguards from the calculated frequency 9.2E-4 /yr. | 5 – Catastrophic | 5 – Almost certain |  |  | BMS-4000 – Reheat furnace BMS flame-failure shut-off (scanners BS-4010, logic BMS-4000, SSOVs XV-4002A/B) | Yes | Furnace draught / post-purge removes unburnt gas through the stack before it can ignite | No | Furnace explosion relief doors; no-go zone around burner platforms during light-off | Yes | [8 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-010 Upgrade the reheat furnace flame-failure shut-off to meet SIL 2 (fault tree FT-GN-03 PFDavg 1.1E-2 = SIL 1 band; event tree ETA-GN-02 explosion frequency 9.2E-4 /yr vs target 1E-4): self-checking UV scanners 1oo2 per burner, proof-tested SSOVs, BMS logic solver to IEC 61511 / EN 746-2. R-012 Bypass / override management for BMS, SIS and gas detectors: authorisation, time limit, logging and monthly audit; BMS logic changes only under MOC. | Instrument engineer / HSE / process safety
| Pressure | MORE |  | Failed-open pressure control valves (PCVs) | Incorrect operation | [5 empty] | Flame lift-off and flame-out (then as N06-01); over-firing – skid / refractory damage [N06-02] BMS not credited separately – the PSHH trip acts through the same logic solver. | 4 – Major | 3 – Possible |  |  | PSHH-4006 – High-high fuel gas pressure trip to BMS-4000 | Yes | BMS-4000 – Reheat furnace BMS flame-failure shut-off (scanners BS-4010, logic BMS-4000, SSOVs XV-4002A/B) | No | [10 empty] | 4 – Major | 2 – Unlikely
| Flow | LESS |  | Line restriction; valve partly closed | Combustion air fan FN-4007 trip / damper closed | [5 empty] | Fuel-rich combustion – CO, unburnt gas accumulating in the furnace; explosion when air is restored [N06-03] Bow tie BT-GN-02 threat T4. | 5 – Catastrophic | 3 – Possible |  |  | FSLL-4008 – Low-low combustion air flow trip (fan FN-4007) to BMS-4000 | Yes | Cross-limited air / fuel ratio control | No | [10 empty] | 5 – Catastrophic | 1 – Rare
| Timing / sequence | BEFORE |  | Purge interlock bypassed / forced | Auto / manual facility and human error | [5 empty] | Light-off into a furnace containing gas from a previous attempt – explosion [N06-04] Bow tie BT-GN-02 threat T3. | 5 – Catastrophic | 3 – Possible |  |  | BMS-4000 purge – BMS pre-purge interlock (≥ 4 volume changes with proven air flow) before light-off | Yes | Light-off procedure OP-RM-040 and checklist; no manual torch lighting | No | [10 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-012 Bypass / override management for BMS, SIS and gas detectors: authorisation, time limit, logging and monthly audit; BMS logic changes only under MOC. | HSE / process safety
| Process gas (CO, H2 – BFG, COG, LD gas, reducing gas) | LEAK OF |  | Poor isolation / passing valves | Isolation failure during maintenance (no double block and bleed, no blinding) | [5 empty] | Gas accumulates in a cold, idle furnace – explosion at the next light-off or hot work; asphyxiation / fire during furnace entry [N06-05] Bow tie BT-GN-02 threat T2; FMECA S06 XV-4002A (leakage in closed position). | 5 – Catastrophic | 3 – Possible |  |  | VPS-4004 – Valve proving system – tightness test of XV-4002A/B before light-off; DBB vent XV-4003 | Yes | Positive isolation (spade / spectacle blind) of fuel gas for furnace entry and extended shutdowns; gas test before entry | No | [10 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-011 Valve proving (VPS-4004) of XV-4002A/B before every light-off; positive isolation (spade) for furnace entry and extended shutdowns (bow tie BT-GN-02 threat 2). | Rolling-mill superintendent
| Process control / instrumentation | LOSS OF |  | Alarm flooding; bypassed trips | Alarm and trip testing not done | Control philosophy unclear |  |  |  |  | Flame-failure, purge or pressure trips not available – as N06-01 / N06-04 [N06-06] Bypass of the BMS is event BE-009 in fault tree FT-GN-03. | 5 – Catastrophic | 3 – Possible |  |  | Bypass / override management – authorised, time-limited, logged; monthly audit | No | Management of change for BMS / SIS logic and set-point changes | No | [10 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-012 Bypass / override management for BMS, SIS and gas detectors: authorisation, time limit, logging and monthly audit; BMS logic changes only under MOC. | HSE / process safety
| Maintenance | INADEQUATE |  | Isolation, drainage, purging | Slip plates | Rescue plan |  |  |  |  | Fire / explosion or asphyxiation of people inside the furnace [N06-07] | 5 – Catastrophic | 2 – Unlikely |  |  | Positive isolation (spade / spectacle blind) of fuel gas for furnace entry and extended shutdowns; gas test before entry | No | Permit-to-work with isolation verification (DBB / spades), gas-free test and fire watch | No | Personal O2 monitors; confined-space entry permit for shelters, pits and furnaces | No | [8 empty] | 5 – Catastrophic | 1 – Rare |  |  | R-011 Valve proving (VPS-4004) of XV-4002A/B before every light-off; positive isolation (spade) for furnace entry and extended shutdowns (bow tie BT-GN-02 threat 2). | Rolling-mill superintendent

## Node 07
HAZOP WORKSHEET
Select node ▸ |  |  | N07 – Purge, vent, blowdown and maintenance isolation | [8 empty] | Session date | 2026-10-13 |  | Revision | A
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by
| Air / oxygen in process gas | AS WELL AS |  | Inadequate purging at start-up / shutdown | Dead legs not purged | [5 empty] | Flammable mixture in the line on gas-in – internal deflagration; flashback at the first burner lit [N07-01] See N03-03. | 5 – Catastrophic | 3 – Possible |  |  | Written purge plan OP-GN-020: N2 purge to O2 < 2 % before gas-in and gas > 90 % at the vent before relight (portable analyser) | No | [12 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-015 Purge plan for every gas-in / gas-out: N2 purge with O2 < 2 % confirmed before gas-in and gas > 90 % confirmed at the vent before relight; calibrated portable analysers. | Operations superintendent
| Inert gas (N2, Ar) | LEAK OF |  | Leak or purge into enclosed or confined area | Pit, tunnel or bin atmosphere not tested before entry | [5 empty] | Asphyxiation of people in the PRS shelter, valve pits or furnace [N07-02] | 5 – Catastrophic | 3 – Possible |  |  | Personal O2 monitors; confined-space entry permit for shelters, pits and furnaces | No | PRS shelter natural ventilation (louvres at high and low level) | No | [10 empty] | 5 – Catastrophic | 2 – Unlikely
| Flow | REVERSE |  | Utility station connected to process (nitrogen hose left connected) | N2 header pressure below gas pressure (7 barg) | [5 empty] | NG in the plant N2 system: flammable gas delivered wherever N2 is used for inerting – including the hot DRI conveyor N2 fire-protection system XS-210 (see the hot DRI conveyor example) [N07-03] FMECA S07 N2-1304; interface with the hot DRI conveyor example. | 5 – Catastrophic | 3 – Possible |  |  | N2-1304 – N2 purge connections by removable spool / hose with check valve and double block & bleed; disconnected after use | No | [12 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-014 N2 purge connections to the gas system by removable spool / hose only, with check valve and double block & bleed; disconnect after use (prevents NG back-flow into the plant N2 header that also feeds the hot DRI conveyor N2 system XS-210). | Utilities manager
| Relief | INADEQUATE |  | Relief valve discharge location unsafe (to work areas, ignition sources) | Pollution implications of discharge | [5 empty] | Cold-vented gas drifts to platforms or the heater flues – flash fire [N07-04] | 4 – Major | 3 – Possible |  |  | VS-1301 – Vent stack VS-1301 3 m above the nearest platform, away from heater flues; N2 snuffing | No | [12 empty] | 4 – Major | 2 – Unlikely |  |  | R-005 Route all regulator pilot / diaphragm vents and the PSV-1105 discharge to vent stack VS-1301 outside the PRS shelter; confirm by dispersion check that the vent is clear of heater flues and platforms. | Process engineer
| Maintenance | INADEQUATE |  | Work permit system | Isolation, drainage, purging | [S] Hot work near gas mains or dust; work under suspended loads; work inside cooled-down furnaces |  |  |  |  | Ignition of gas at the work site – fire, burns [N07-05] Bow tie BT-GN-01 threat T5. | 4 – Major | 3 – Possible |  |  | Permit-to-work with isolation verification (DBB / spades), gas-free test and fire watch | No | Hot-tapping procedure (minimum flow, wall-thickness check, specialist contractor) | No | [10 empty] | 4 – Major | 2 – Unlikely
| Operator action | NO |  | Drain or vent valves left open | Valve line-up not checked after maintenance | [5 empty] | Gas released through an open vent or blind flange on gas-in [N07-06] | 4 – Major | 3 – Possible |  |  | Valve line-up checklist and spectacle-blind register | No | Operator rounds with portable gas detector; annual acoustic leak survey | No | [10 empty] | 4 – Major | 2 – Unlikely |  |  | R-015 Purge plan for every gas-in / gas-out: N2 purge with O2 < 2 % confirmed before gas-in and gas > 90 % confirmed at the vent before relight; calibrated portable analysers. | Operations superintendent

## Node 08
HAZOP WORKSHEET
Select node ▸ |  |  | N08 – Gas detection, F&G and ESD system | [8 empty] | Session date | 2026-10-14 |  | Revision | A
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by
| Process control / instrumentation | LOSS OF |  | Alarm and trip testing not done | Location of instruments unsuitable | Fire protection of instruments and cables |  |  |  |  | A gas release in the GRMS / PRS is not isolated – the pipeline and MP inventory feed the release: prolonged jet fire, larger vapour cloud (event tree ETA-GN-01) [N08-01] Quantified: fault tree FT-GN-02 PFDavg 2.6E-2 (RRF 38); used by event tree ETA-GN-01 heading H2 and bow tie BT-GN-01 mitigative barrier. Likelihood after safeguards from the calculated frequency 4.3E-6 /yr. | 5 – Catastrophic | 3 – Possible |  |  | Proof testing – quarterly gas detector bump tests, annual full-stroke ESD valve tests, annual logic test | No | HS-1000 – Manual ESD push buttons (control room and field) – operator response to gas alarms and reports | No | [10 empty] | 5 – Catastrophic | 1 – Rare |  |  | R-001 Verify the HP / MP gas detection & ESD function against the required risk reduction. Fault tree FT-GN-02 gives PFDavg 2.6E-2 (RRF 38); test the effect of six-monthly partial-stroke testing of ESDV-1001 / ESDV-1107 and quarterly detector bump tests (FMECA S01 / S08). R-020 Gas alarm response procedure and drills – the manual ESD is credited in fault tree FT-GN-02 (gate G-004) with an operator failure probability of 0.1. | Instrument engineer / Operations superintendent
| Utilities / services | LOSS OF |  | Power | UPS battery failure | [5 empty] | Fail-safe design closes the ESD valves – loss of gas to the whole works (flame-outs, see N02-03); if the UPS fails while a release occurs, no automatic isolation [N08-02] FMECA S08 UPS-1000. | 3 – Moderate | 3 – Possible |  |  | UPS-1000 – UPS for SIS / F&G (30 min) with alarm; de-energise-to-trip (fail-safe) design | No | PSLL-2006 / PSLL-4005 – Low-low gas pressure trips in the user burner management systems (reformer, reheat furnace, preheaters) | Yes | [10 empty] | 3 – Moderate | 2 – Unlikely
| Operator action | NO |  | Time available for operator intervention | Alarm flooding; bypassed trips | [5 empty] | Release not isolated when the automatic function has failed (as N08-01) [N08-03] Fault tree FT-GN-02 gate G-004 (manual ESD) – operator failure 0.1. | 5 – Catastrophic | 3 – Possible |  |  | Gas alarm response procedure and emergency drills | No | [12 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-020 Gas alarm response procedure and drills – the manual ESD is credited in fault tree FT-GN-02 (gate G-004) with an operator failure probability of 0.1. | Operations superintendent
| Maintenance | INADEQUATE |  | Calibration | Training | Condition monitoring |  |  |  |  | Detection unavailable – as N08-01 [N08-04] FMECA S08 GD-1110A (drift); common-cause group CCF-001 in FT-GN-02. | 5 – Catastrophic | 3 – Possible |  |  | Proof testing – quarterly gas detector bump tests, annual full-stroke ESD valve tests, annual logic test | No | Bypass / override management – authorised, time-limited, logged; monthly audit | No | [10 empty] | 5 – Catastrophic | 2 – Unlikely |  |  | R-001 Verify the HP / MP gas detection & ESD function against the required risk reduction. Fault tree FT-GN-02 gives PFDavg 2.6E-2 (RRF 38); test the effect of six-monthly partial-stroke testing of ESDV-1001 / ESDV-1107 and quarterly detector bump tests (FMECA S01 / S08). R-012 Bypass / override management for BMS, SIS and gas detectors: authorisation, time limit, logging and monthly audit; BMS logic changes only under MOC. | Instrument engineer / HSE / process safety

## Node 09
HAZOP WORKSHEET
Select node ▸ | [11 empty] | Session date |  |  | Revision
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by

## Node 10
HAZOP WORKSHEET
Select node ▸ | [11 empty] | Session date |  |  | Revision
Node title
P&IDs / drawings
Battery limits
Functional description / design intent
Design parameters
Operating parameters
ONE ROW PER DEVIATION. Choose Parameter + Guideword, then pick up to 6 causes in Cause 1–6 (or type your own) – they are listed line by line in 'Potential causes'. Enter up to 6 safeguards, each marked IPL Yes/No – listed in 'Safeguards'. Use the [–] buttons above the columns to collapse the pick columns.
DEVIATION |  |  |  | CAUSE PICK-LIST | [5 empty] | CAUSES & CONSEQUENCES |  | RISK BEFORE SAFEGUARDS |  |  |  | SAFEGUARD ENTRY (mark each IPL Yes / No) | [11 empty] | SAFEGUARDS |  | RISK AFTER SAFEGUARDS |  |  |  | RECOMMENDATIONS
Dev. No. | Parameter | Guideword | Deviation | Cause 1 | Cause 2 | Cause 3 | Cause 4 | Cause 5 | Cause 6 | Potential causes | Consequences | Severity (S) | Likelihood (L) | Risk score | Risk rank | Safeguard 1 | IPL? 1 | Safeguard 2 | IPL? 2 | Safeguard 3 | IPL? 3 | Safeguard 4 | IPL? 4 | Safeguard 5 | IPL? 5 | Safeguard 6 | IPL? 6 | Safeguards | No. of IPLs | Severity (S) | Likelihood (L) | Risk score | Risk rank | Recommendations / actions | Action by